## Sheet1
Name | Description | Image
Tripp Lite series SmartRack 42U Standard-Depth Rack Enclosure Cabinet with Doors and Side Panels | 42U rack constructed from powder-coated steel that stands up to tough environments Maximum capacity: 3500 lb. (1588 kg) stationary, 2250 lb. (1021 kg) rolling load Doors and side panels lock securely to help prevent damage, tampering or theft Ships fully assembled for immediate deployment and equipment mounting Provides physical equipment and media security required for PCI DSS compliance 5-year limited warranty. Also available in SR42UBG,SR42UBWDVRT,SR42UBWD, SR42UBWDSP1,SR42UB1032,SR42UBKD, SR25UB,SR48UBDPWD8,SR48UBWD8,SR42UBWD8, SR42UBDPWD8,SR45UBDPWD,SR25UBSP1, SR42UBEVS,SR42UBMD,SR42UBSD,SR45UB, SR45UBMD,SR45UBSD,SR45UBSP1,SR45UBWD, SR45UBWDSP1,SR45UBWDVRT,SR48UB, SR48UBWD,SR48UBWDSP1,SR42UBEIS
Tripp Lite series 42U SmartRack Co-Location Standard-Depth Rack Enclosure Cabinet - 2 separate compartments | Two compartment co-location rack with doors and side panels 4 interior vertical posts with unthreaded square hole openings Standard 24" width for optimizing floor space Features a secure cable channel for each individual compartment Ships fully assembled Massive front to rear ventilation capacity 3500 lbs (1588 kgs) stationary / 2250 lbs (1020.6 kgs) rolling load capacity Locking, removable, reversible front and rear doors Combination lock, with key override standard on all doors Locking, removable side panels keyed alike with doors Meets all enclosure requirements towards PCI DSS (Payment Card Industry Data Security Standard) Compliance 5-year limited warranty. Also available in SR48UBCL
Tripp Lite series 42U SmartRack Standard-Depth Rack Enclosure Cabinet with doors, side panels & shock pallet shipping | Standard 42U SmartRack enclosure with additional shock pallet and loading ramps. 4 interior vertical posts with unthreaded square hole openings Standard 24" (600mm) width and 42" (1050mm) depth for optimizing floor space Ships fully assembled Massive front to rear ventilation capacity 3500 lbs (1588 kgs) stationary / 2250 lbs (1020.6 kgs) rolling load capacity Locking, removable, reversible front and rear doors Locking, removable side panels keyed alike with doors Meets all enclosure requirements towards PCI DSS (Payment Card Industry Data Security Standard) Compliance 5-year limited warranty. Also available in SR48UBSP1
Tripp Lite series 42U Standard-Depth 4-Post Premium Open Frame Rack - No Doors or Side Panels | 42U premium open frame rack includes no sides or doors 4 interior vertical posts with unthreaded square hole openings Standard 24 in. (600 mm) width and 42 in. (1050 mm) depth for optimizing floor space Ships fully assembled for use right away 3500 lbs (1588 kgs) stationary and 2250 lbs (1020.6 kgs) rolling load capacity Preinstalled heavy-duty 3 in. casters and leveling feet Designed to roll through a standard 7-ft. (2.13 m) doorway Includes 50 M6 cage nuts and 50 M6 screws for mounting equipment 5-year limited warranty Also Available in SR42UBEXPNDNR3
Tripp Lite series 42U SmartRack Seismic-Certified Standard-Depth Rack Enclosure Cabinet with doors & side panels | Tested to NEBS Seismic Zone 4 requirements 42U SmartRack enclosure with doors and side panels 4 interior vertical posts with unthreaded square hole mounting Standard 24" width for optimizing floor space Ships fully assembled Massive front to rear ventilation capacity Locking, removable side panels keyed alike with doors Includes 50 pieces of M6 cage nuts and 50 pieces of M6 screws (equipment mounting hardware) Baying brackets and hardware included Meets all enclosure requirements towards PCI DSS (Payment Card Industry Data Security Standard) Compliance 5-year limited warranty
Tripp Lite series SmartRack 6U Low-Profile Switch-Depth Wall-Mount Mini Rack Enclosure | Houses, secures and organizes switches and other rack-mount equipment in server closets, classrooms, offices and other areas with limited floor space. 6U rack constructed from powder-coated steel that stands up to tough environments Houses switches, routers and other equipment up to maximum 200 lb. load capacity Doors and side panels lock securely to help prevent damage, tampering or theft Ships fully assembled for immediate deployment and equipment mounting Provides physical equipment and media security required for PCI DSS compliance 5-year limited warranty. Also available SRW9U,SRW12U,SRW12UG
SRW9UG | UPC Code - 037332187291 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type Small - Enclosure PHYSICAL Color - Black Rack Height - 9U Rack Depth - Shallow Maximum Device Depth (cm) - 41.91 Maximum Device Depth (in.) - 16.5 Maximum Device Depth (mm) - 419 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 26.10 x 22.70 x 20.10 Shipping Dimensions (hwd / cm) - 66.29 x 57.66 x 51.05 Shipping Weight (lbs.) - 40.00 Shipping Weight (kg) - 18.14 Unit Dimensions (hwd / in.) - 19.750 x 23.630 x 17.690 Unit Dimensions (hwd / cm) - 50,17 x 60,02 x 45 Unit Weight (lbs.) - 34.6 Unit Weight (kg) - 15.69 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 2 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Certifications - UL 60950-1 Product Compliance - RoHS; EIA/ECA-310-E; UKCA
SRW12US | UPC Code - 037332148674 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Small Enclosure PHYSICAL Color - Black Rack Height - 12U Rack Depth - Shallow Factory Preset Rack Depth (in.) - 10.42 Factory Preset Rack Depth (cm) - 26.5 Factory Preset Rack Depth (mm) - 265 Maximum Device Depth (cm) - 52.07 Maximum Device Depth (in.) - 20.5 Maximum Device Depth (mm) - 521 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 24.30 x 26.00 x 27.80 Shipping Dimensions (hwd / cm) - 61.72 x 66.04 x 70.61 Shipping Weight (lbs.) - 64.00 Shipping Weight (kg) - 29.03 Unit Dimensions (hwd / in.) - 24.625 x 23.500 x 21.625 Unit Dimensions (hwd / cm) - 63.5 x 60 x 54.86 Unit Weight (lbs.) - 60 Unit Weight (kg) - 27.22 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Compliance - RoHS; EIA/ECA-310-E; UKCA
SRW12USNEMA | UPC Code - 037332168016 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Small Enclosure INPUT Nominal Input Voltage(s) Supported - 120V AC Nominal Input Voltage Description - 120V 50/60 Hz Input Plug Type - NEMA 5-15P Input Cord Length (ft.) - 6 Input Cord Length (m) - 1.83 PHYSICAL Color - Black Rack Height - 12U Rack Depth - Shallow Factory Preset Rack Depth (in.) - 10.42 Factory Preset Rack Depth (cm) - 26.5 Factory Preset Rack Depth (mm) - 265 Maximum Device Depth (cm) - 52.07 Maximum Device Depth (in.) - 20.5 Maximum Device Depth (mm) - 521 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Shipping Dimensions (hwd / in.) - 28.00 x 26.00 x 29.00 Shipping Dimensions (hwd / cm) - 71.12 x 66.04 x 73.66 Shipping Weight (lbs.) - 90.00 Shipping Weight (kg) - 40.82 Unit Dimensions (hwd / in.) - 25.000 x 23.630 x 21.600 Unit Dimensions (hwd / cm) - 63.5 x 60 x 54.86 Unit Weight (lbs.) - 60 Unit Weight (kg) - 27.22 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Built-in Cable Management - No Extra Wide - No Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Compliance - RoHS; EIA/ECA-310-E SRWX12USNEMA
SRW12UDP | UPC Code - 037332191472 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Small Enclosure PHYSICAL Color - Black Rack Height - 12U Rack Depth - Shallow Maximum Device Depth (cm) - 52.07 Maximum Device Depth (in.) - 20.5 Maximum Device Depth (mm) - 521 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 29.72 x 28.75 x 26.57 Shipping Dimensions (hwd / cm) - 75.49 x 73.02 x 67.49 Shipping Weight (lbs.) - 57.00 Shipping Weight (kg) - 25.85 Unit Dimensions (hwd / in.) - 25.080 x 23.620 x 21.750 Unit Dimensions (hwd / cm) - 63,70 x 60,00 x 55,25 Unit Weight (lbs.) - 58.4 Unit Weight (kg) - 26.49 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Compliance - RoHS; EIA/ECA-310-E. Also available in SRW15US
SRW10US | UPC Code - 037332154828 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Small Enclosure PHYSICAL Color - Black Rack Height - 10U Rack Depth - Shallow Factory Preset Rack Depth (in.) - 10.42 Factory Preset Rack Depth (cm) - 26.5 Factory Preset Rack Depth (mm) - 265 Maximum Device Depth (cm) - 52.07 Maximum Device Depth (in.) - 20.5 Maximum Device Depth (mm) - 521 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 24.25 x 26.38 x 24.13 Shipping Dimensions (hwd / cm) - 61.60 x 67.01 x 61.29 Shipping Weight (lbs.) - 59.00 Shipping Weight (kg) - 26.76 Unit Dimensions (hwd / in.) - 21.560 x 23.630 x 21.630 Unit Dimensions (hwd / cm) - 54.79 x 59.99 x 54.86 Unit Weight (lbs.) - 55 Unit Weight (kg) - 24.95 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Compliance - RoHS; EIA/ECA-310-E; UKCA
SRW6UDP | UPC Code - 037332191458 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Small Enclosure PHYSICAL Color - Black Rack Height - 6U Rack Depth - Shallow Maximum Device Depth (cm) - 52.07 Maximum Device Depth (in.) - 20.5 Maximum Device Depth (mm) - 521 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 20.00 x 27.00 x 30.00 Shipping Dimensions (hwd / cm) - 50.80 x 68.58 x 76.20 Shipping Weight (lbs.) - 44.00 Shipping Weight (kg) - 19.96 Unit Dimensions (hwd / in.) - 14.570 x 23.620 x 21.710 Unit Dimensions (hwd / cm) - 37.01 x 59.99 x 55.14 Unit Weight (lbs.) - 45.2 Unit Weight (kg) - 20.50 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Compliance - RoHS; EIA/ECA-310-E
SRW10USG | UPC Code - 037332187345 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Small Enclosure PHYSICAL Color - Black Rack Height - 10U Rack Depth - Shallow Factory Preset Rack Depth (in.) - 10.42 Factory Preset Rack Depth (cm) - 26.5 Factory Preset Rack Depth (mm) - 265 Maximum Device Depth (cm) - 52.07 Maximum Device Depth (in.) - 20.5 Maximum Device Depth (mm) - 521 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Shipping Dimensions (hwd / in.) - 24.25 x 26.38 x 24.13 Shipping Dimensions (hwd / cm) - 61.60 x 67.01 x 61.29 Shipping Weight (lbs.) - 59.00 Shipping Weight (kg) - 26.76 Unit Dimensions (hwd / in.) - 21.560 x 23.630 x 21.630 Unit Dimensions (hwd / cm) - 54.77 x 60.02 x 59.94 Unit Weight (lbs.) - 53.4 Unit Weight (kg) - 24.22 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Compliance - RoHS; EIA/ECA-310-E
SRW6UDPGVRT | UPC Code - 037332214256 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Small Enclosure PHYSICAL Color - Black Rack Height - 6U Rack Depth - Shallow Maximum Device Depth (cm) - 52.07 Maximum Device Depth (in.) - 20.5 Maximum Device Depth (mm) - 521 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 17.72 x 24.40 x 32.28 Shipping Weight (kg) - 22.68 Unit Dimensions (hwd / in.) - 14.580 x 29.622 x 21.713 Unit Dimensions (hwd / cm) - 37.01 x 75.23 x 55.14 Unit Weight (lbs.) - 44.5 Unit Weight (kg) - 20.18 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Built-in Cable Management - Yes Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Compliance - RoHS; EIA/ECA-310-E
SRW6UDPVRT | UPC Code - 037332236470 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Small Enclosure PHYSICAL Color - Black Rack Height - 6U Rack Depth - Shallow Maximum Device Depth (cm) - 52.07 Maximum Device Depth (in.) - 20.5 Maximum Device Depth (mm) - 521 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 17.72 x 24.40 x 32.28 Shipping Dimensions (hwd / cm) - 45.01 x 61.98 x 81.99 Shipping Weight (lbs.) - 48.00 Shipping Weight (kg) - 21.77 Unit Dimensions (hwd / in.) - 14.580 x 29.622 x 21.713 Unit Dimensions (hwd / cm) - 37.01 x 75.24 x 55.14 Unit Weight (lbs.) - 45.2 Unit Weight (kg) - 20.50 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Built-in Cable Management - Yes Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Compliance - RoHS; EIA/ECA-310-E
SRW9UDPGVRT | UPC Code - 037332214263 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Small Enclosure PHYSICAL Color - Black Rack Height - 9U Rack Depth - Shallow Maximum Device Depth (cm) - 52.07 Maximum Device Depth (in.) - 20.5 Maximum Device Depth (mm) - 521 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 23.03 x 24.40 x 32.28 Shipping Dimensions (hwd / cm) - 58.50 x 61.98 x 81.99 Shipping Weight (lbs.) - 58.86 Shipping Weight (kg) - 26.70 Unit Dimensions (hwd / in.) - 19.830 x 29.622 x 21.710 Unit Dimensions (hwd / cm) - 50.37 x 75.24 x 55.14 Unit Weight (lbs.) - 53.130 Unit Weight (kg) - 24.10 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Built-in Cable Management - Yes Extra Wide - No Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Compliance - RoHS; EIA/ECA-310-E. Also available in SRW9UDPVRT
SRW9UDP | UPC Code - 037332191465 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Small Enclosure PHYSICAL Color - Black Rack Height - 9U Rack Depth - Shallow Maximum Device Depth (cm) - 52.07 Maximum Device Depth (in.) - 20.5 Maximum Device Depth (mm) - 521 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 24.41 x 28.75 x 26.57 Shipping Dimensions (hwd / cm) - 62.00 x 73.02 x 67.49 Shipping Weight (lbs.) - 49.00 Shipping Weight (kg) - 22.23 Unit Dimensions (hwd / in.) - 19.830 x 23.620 x 21.710 Unit Dimensions (hwd / cm) - 50.37 x 59.99 x 55.14 Unit Weight (lbs.) - 51.8 Unit Weight (kg) - 23.50 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Compliance - RoHS; EIA/ECA-310-E
SRW9UDPW | UPC Code - 037332256065 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Small Enclosure PHYSICAL Color - White Rack Height - 9U Rack Depth - Shallow Maximum Device Depth (cm) - 52.07 Maximum Device Depth (in.) - 20.5 Maximum Device Depth (mm) - 521 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 24.41 x 28.75 x 26.57 Shipping Weight (kg) - 22.23 Unit Dimensions (hwd / in.) - 19.830 x 23.620 x 21.710 Unit Dimensions (hwd / cm) - 50.37 x 59.99 x 55.14 Unit Weight (lbs.) - 51.8 Unit Weight (kg) - 23.50 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Built-in Cable Management - No Extra Wide - No Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Compliance - RoHS; EIA/ECA-310-E. Also availble in SRW6UW,SRW6UWG
SRW6UKD | UPC Code - 037332191564 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Small Enclosure PHYSICAL Color - Black Rack Height - 6U Rack Depth - Shallow Maximum Device Depth (cm) - 41.91 Maximum Device Depth (in.) - 16.5 Maximum Device Depth (mm) - 419 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 25.98 x 20.28 x 7.08 Shipping Dimensions (hwd / cm) - 65.99 x 51.51 x 17.98 Shipping Weight (lbs.) - 30.00 Shipping Weight (kg) - 13.61 Unit Dimensions (hwd / in.) - 14.449 x 23.630 x 17.547 Unit Dimensions (hwd / cm) - 36.7 x 60.02 x 44.57 Unit Weight (lbs.) - 29 Unit Weight (kg) - 13.15 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 2 Assembly Required - Yes FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Built-in Cable Management - No Extra Wide - No Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Certifications - UL 60950-1 Product Compliance - RoHS; EIA/ECA-310-E
SRW6UG | UPC Code - 037332187277 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Small Enclosure PHYSICAL Color - Black Rack Height - 6U Rack Depth - Shallow Maximum Device Depth (cm) - 41.91 Maximum Device Depth (in.) - 16.5 Maximum Device Depth (mm) - 419 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 17.30 x 25.80 x 19.90 Shipping Dimensions (hwd / cm) - 43.94 x 65.53 x 50.55 Shipping Weight (lbs.) - 35.00 Shipping Weight (kg) - 15.88 Unit Dimensions (hwd / in.) - 14.500 x 23.500 x 17.500 Unit Dimensions (hwd / cm) - 36.83 x 59.7 x 44.45 Unit Weight (lbs.) - 29 Unit Weight (kg) - 13.15 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 2 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Certifications - UL 60950-1 Product Compliance - RoHS; EIA/ECA-310-E
SRW21U | UPC Code - 037332187321 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Half-Height Enclosure PHYSICAL Color - Black Rack Height - 21U Rack Depth - Shallow Maximum Device Depth (cm) - 41.91 Maximum Device Depth (in.) - 16.5 Maximum Device Depth (mm) - 419 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) = 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 45.87 x 26.61 x 18.98 Shipping Dimensions (hwd / cm) - 116.51 x 67.59 x 48.21 Shipping Weight (lbs.) - 64.00 Shipping Weight (kg) - 29.03 Unit Dimensions (hwd / in.) - 40.870 x 23.630 x 17.720 Unit Dimensions (hwd / cm) - 103.81 x 60.02 x 45.01 Unit Weight (lbs.) - 51.00 Unit Weight (kg) - 23.13 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 2 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Certifications - UL 60950-1 Product Compliance - RoHS; EIA/ECA-310-E; UKCA
SRW21UG | UPC Code - 037332187338 Device Compatibility - Patch Panel; Network Switch; UPS Rack Type - Half-Height Enclosure PHYSICAL Color - Black Rack Height - 21U Rack Depth - Shallow Maximum Device Depth (cm) - 41.91 Maximum Device Depth (in.) - 16.5 Maximum Device Depth (mm) - 419 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Cable Access Hole Measurement (inches) - 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) - 46.10 x 18.70 x 24.50 Shipping Dimensions (hwd / cm) - 117.09 x 47.50 x 62.23 Shipping Weight (lbs.) - 68.00 Shipping Weight (kg) - 30.84 Unit Dimensions (hwd / in.) - 40.870 x 23.630 x 17.720 Unit Dimensions (hwd / cm) - 103.81 x 60.02 x 45.01 Unit Weight (lbs.) - 51.2 Unit Weight (kg) - 23.22 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 2 FEATURES & SPECIFICATIONS Grounding Details - Front and Back door frames Pre-Installed Casters - No STANDARDS & COMPLIANCE Product Certifications - UL 60950-1 Product Compliance - RoHS; EIA/ECA-310-E; UKCA
SRN4G6U | UPC - Code 037332273109 Device Compatibility - Computer; DVR; Network Switch; PDU; Patch Panel; Server; UPS Rack Type - Small Enclosure PHYSICAL Color - -Gray Material of Construction - Powder Coated Steel Rack Height - 6U Rack Depth - Shallow Mounting Location - Wall Factory Preset Rack Depth (in.) - 20.00 Factory Preset Rack Depth (cm) - 50.8 Factory Preset Rack Depth (mm) - 508 Mounting Holes or Slots - Yes Maximum Device Depth (cm) - 41.91 Maximum Device Depth (in.) - -16.5 Maximum Device Depth (mm) - 419 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Shipping Form Factor - Factory Assembled Shipping Dimensions (hwd / in.) - 21.50 x 28.00 x 24.00 Shipping Dimensions (hwd / cm) - 54.61 x 71.12 x 60.96 Shipping Weight (lbs.) - 100.00 Shipping Weight (kg) - 45.36 Unit Dimensions (hwd / in.) - 13.580 x 24.000 x 18.660 Unit Dimensions (hwd / cm) - 34.49 x 60.96 X 47.40 Unit Dimensions (in.) - 13.580 x 24.000 x 18.660 Unit Weight (lbs.) - 57.6 Unit Weight (kg) - 26.13 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 Mounting Details - Adjustable equipment mounting rail (10-32) Cable Entry/Exit - Sealed cut-out; compatible gland plates sold separately. FEATURES & SPECIFICATIONS Grounding Details - Cabinet Body Tools Necessary - Yes Built-in Cable Management - No Extra Wide - No Locking - Yes Lock Type - Key Pre-Installed Casters - No Outdoor Use - Yes Gasketed Door - Yes STANDARDS & COMPLIANCE Protection Rating NEMA - 4 Product Certifications - CAN/CSA-C22.2 No. 286 (Canada); UL 508A Product Compliance - EIA/ECA-310-E; NEMA 4; RoHS; REACH
SRIN4101010 | UPC Code - 037332282453 Device Compatibility - Patch Panel; Network Switch Rack Type - Enclosure; Small Enclosure PHYSICAL Color - Gray Material of Construction - Powder Coated Steel Rack Height - 5U Rack Depth - Mid Mounting Location - Wall; Pole Mounting Holes or Slots - Yes Maximum Device Depth (cm) - 22.86 Maximum Device Depth (in.) - 9 Maximum Device Depth (mm) - 229 Shipping Form Factor - Factory Assembled Shipping Dimensions (hwd / in.) - 12.40 x 12.40 x 12.40 Shipping Dimensions (hwd / cm) - 31.50 x 31.50 x 31.50 Shipping Weight (lbs.) - 23.15 Shipping Weight (kg) - 10.50 Unit Dimensions (hwd / in.) - 10.000 x 10.000 x 10.000 Unit Dimensions (hwd / cm) - 25.4 x 25.4 x 25.4 Unit Dimensions (in.) - 10 x 10 x 10 Unit Weight (lbs.) - 17.64 Unit Weight (kg) - 8.00 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Mounting Details - Plastic and metal mounting panel, document holder Cable Entry/Exit - Cut-out with removeable cover FEATURES & SPECIFICATIONS Grounding Details - Cabinet Body Tools Necessary - Yes Built-in Cable Management - No Extra Wide - No Locking - Yes Lock Type - Key Pre-Installed Casters - No Outdoor Use - Yes Gasketed Door - Yes STANDARDS & COMPLIANCE Protection Rating - -NEMA 4 Product Certifications - CAN/CSA-C22.2 No. 286 (Canada); CAN/CSA-C22.2 No. 94 (Canada); UL 50; UL 508A Product Compliance - NEMA 4; RoHS; REACH. Also available in SRIN410106,SRIN4121210,SRIN412126,SRIN4141410, SRIN414146
SRIN4181810R | UPC Code - 037332282675 Device Compatibility - Patch Panel; Network Switch Rack Type - Small Enclosure PHYSICAL Color - Red Material of Construction - Powder Coated Steel Rack Height - 10U Rack Depth - Mid Mounting Location - Wall; Pole Mounting Holes or Slots - Yes Maximum Device Depth (cm) - 22.86 Maximum Device Depth (in.) - 9 Maximum Device Depth (mm) - 229 Shipping Form Factor - Factory Assembled Shipping Dimensions (hwd / in.) - 12.40 x 20.27 x 20.27 Shipping Weight (kg) - 20.50 Unit Dimensions (hwd / in.) - 18.000 x 18.000 x 10.000 Unit Dimensions (hwd / cm) - 45.72 x 45.72 x 25.4 Unit Dimensions (in.) - 18 x 18 x 10 Unit Weight (lbs.) - 35.27 Unit Weight (kg) - 16.00 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 Mounting Details - Plastic and metal mounting panel, document holder Cable Entry/Exit - Cut-out with removeable cover FEATURES & SPECIFICATIONS Grounding Details - Cabinet Body Tools Necessary - Yes Built-in Cable Management - No Extra Wide - No Locking - Yes Lock Type - Key Pre-Installed Casters - No Outdoor Use - Yes Gasketed Door - Yes STANDARDS & COMPLIANCE Protection Rating - NEMA 4 Product Certifications - CAN/CSA-C22.2 No. 286 (Canada); CAN/CSA-C22.2 No. 94 (Canada); UL 50; UL 508A Product Compliance - NEMA 4; RoHS; REACH
SRIN4181810 | UPC Code - 037332282378 Device Compatibility - Patch Panel; Network Switch Rack Type - Small Enclosure PHYSICAL Color - Gray Material of Construction - Powder Coated Steel Rack Height - 10U Rack Depth - Mid Mounting Location - Wall; Pole Mounting Holes or Slots - Yes Maximum Device Depth (cm) - 22.86 Maximum Device Depth (in.) - 9 Maximum Device Depth (mm) - 229 Shipping Form Factor - Factory Assembled Shipping Dimensions (hwd / in.) - 12.40 x 20.27 x 20.27 Shipping Weight (kg) - 20.50 Unit Dimensions (hwd / in.) - 18.000 x 18.000 x 10.000 Unit Dimensions (hwd / cm) - 45.72 x 45.72 x 25.4 Unit Dimensions (in.) - 18 x 18 x 10 Unit Weight (lbs.) - 35.27 Unit Weight (kg) - 16.00 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Mounting Details - Plastic and metal mounting panel, document holder Cable Entry/Exit - Cut-out with removeable cover FEATURES & SPECIFICATIONS Grounding Details - Cabinet Body Tools Necessary - Yes Built-in Cable Management - No Extra Wide - No Locking - Yes Lock Type - Key Pre-Installed Casters - No Outdoor Use - Yes Gasketed Door - Yes STANDARDS & COMPLIANCE Protection Rating - NEMA 4 Product Certifications - CAN/CSA-C22.2 No. 286 (Canada); CAN/CSA-C22.2 No. 94 (Canada); UL 50; UL 508A Product Compliance - NEMA 4; RoHS; REACH Also available in SRIN418186
SRIN410106R | UPC Code - 037332283061 Device Compatibility - Patch Panel; Network Switch Rack Type - Enclosure; Small Enclosure PHYSICAL Color - Red Material of Construction - Powder Coated Steel Rack Height - 5U Rack Depth - Shallow Mounting Location - Wall; Pole Mounting Holes or Slots - Yes Maximum Device Depth (cm) - 22.86 Maximum Device Depth (in.) - 9 Maximum Device Depth (mm) - 229 Shipping Form Factor - Factory Assembled Shipping Dimensions (hwd / in.) - 12.40 x 12.40 x 12.40 Shipping Weight (kg) - 10.50 Unit Dimensions (hwd / in.) - 10.000 x 10.000 x 6.000 Unit Dimensions (hwd / cm) - 25.4 x 25.4 x 15.24 Unit Dimensions (in.) - 10 x 10 x 6 Unit Weight (lbs.) - 17.64 Unit Weight (kg) - 8.00 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 Mounting Details - Plastic and metal mounting panel, document holder Cable Entry/Exit - Cut-out with removeable cover FEATURES & SPECIFICATIONS Grounding Details - Cabinet Body Tools Necessary - Yes Built-in Cable Management - No Extra Wide - No Locking - Yes Lock Type - Key Pre-Installed Casters - No Outdoor Use - Yes Gasketed Door - Yes STANDARDS & COMPLIANCE Protection Rating - NEMA 4 Product Certifications - CAN/CSA-C22.2 No. 286 (Canada); CAN/CSA-C22.2 No. 94 (Canada); UL 50; UL 508A Product Compliance - NEMA 4; RoHS; REACH
SRIN410106Y | UPC Code - 037332283078 Device Compatibility - Patch Panel; Network Switch Rack Type - Enclosure; Small Enclosure PHYSICAL Color - Yellow Material of Construction - Powder Coated Steel Rack Height - 5U Rack Depth - Shallow Mounting Location - Wall; Pole Mounting Holes or Slots - Yes Maximum Device Depth (cm) - 22.86 Maximum Device Depth (in.) - 9 Maximum Device Depth (mm) - 229 Shipping Form Factor - Factory Assembled Shipping Dimensions (hwd / in.) - 12.40 x 12.40 x 12.40 Shipping Weight (kg) - 10.50 Unit Dimensions (hwd / in.) - 10.000 x 10.000 x 6.000 Unit Dimensions (hwd / cm) - 25.4 x 25.4 x 15.24 Unit Dimensions (in.) - 10 x 10 x 6 Unit Weight (lbs.) - 17.64 Unit Weight (kg) - 8.00 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 Mounting Details - Plastic and metal mounting panel, document holder Cable Entry/Exit - Cut-out with removeable cover FEATURES & SPECIFICATIONS Grounding Details - Cabinet Body Tools Necessary - Yes Built-in Cable Management - No Extra Wide - No Locking - Yes Lock Type - Key Pre-Installed Casters - No Outdoor Use - Yes Gasketed Door - Yes STANDARDS & COMPLIANCE Protection Rating - NEMA 4 Product Certifications - CAN/CSA-C22.2 No. 286 (Canada); CAN/CSA-C22.2 No. 94 (Canada); UL 50; UL 508A Product Compliance - NEMA 4; RoHS; REACH
SRN4G12US | UPC Code - 037332277169 Device Compatibility - DVR; Network Switch; PDU; Patch Panel; UPS Rack Type - Enclosure PHYSICAL Color - Gray Material of Construction - Powder Coated Steel Rack Height - 12U Rack Depth - Shallow Mounting Location - Wall Factory Preset Rack Depth (in.) - 20.00 Factory Preset Rack Depth (cm) - 50.8 Factory Preset Rack Depth (mm) - 508 Mounting Holes or Slots - Yes Maximum Device Depth (cm) - 71.12 Maximum Device Depth (in.) - 28 Maximum Device Depth (mm) - 711 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Shipping Form Factor - Factory Assembled Shipping Dimensions (hwd / in.) - 30.00 x 28.00 x 34.00 Shipping Dimensions (hwd / cm) - 76.20 x 71.12 x 86.36 Shipping Weight (lbs.) - 175.00 Shipping Weight (kg) - 79.38 Unit Dimensions (hwd / in.) - 24.080 x 24.000 x 30.050 Unit Dimensions (hwd / cm) - 61.163 x 61.163 X 76.327 Unit Dimensions (in.) - 24.080 x 24.000 x 30.050 Unit Weight (lbs.) - 122.05 Unit Weight (kg) - 55.36 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 Mounting Details - Adjustable equipment mounting rail (10-32) Cable Entry/Exit - Sealed cut-out; compatible gland plates sold separately. FEATURES & SPECIFICATIONS Grounding Details - Cabinet Body Tools Necessary - Yes Built-in Cable Management - No Extra Wide - No Locking - Yes Lock Type - Key Pre-Installed Casters - No Outdoor Use - Yes Gasketed Door - Yes STANDARDS & COMPLIANCE Protection Rating - NEMA 4 Product Certifications - CAN/CSA-C22.2 No. 286 (Canada); UL 508A Product Compliance - EIA/ECA-310-E; NEMA 4; RoHS; REACH
SRN4G6US | UPC Code - 037332277138 Device Compatibility - DVR; Network Switch; PDU; Patch Panel; UPS Rack Type - Small Enclosure PHYSICAL Color - Gray Material of Construction - Powder Coated Steel Rack Height - 6U Rack Depth - Mid Mounting Location - Wall Factory Preset Rack Depth (in.) - 20.00 Factory Preset Rack Depth (cm) - 50.8 Factory Preset Rack Depth (mm) - 508 Mounting Holes or Slots - Yes Maximum Device Depth (cm) - n71.12 Maximum Device Depth (in.) - 28 Maximum Device Depth (mm) - 711 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Shipping Form Factor - Factory Assembled Shipping Dimensions (hwd / in.) - 19.00 x 28.00 x 34.00 Shipping Dimensions (hwd / cm) - 48.26 x 71.12 x 86.36 Shipping Weight (lbs.) - 140.00 Shipping Weight (kg) - 63.50 Unit Dimensions (hwd / in.) - 13.580 x 24.000 x 30.050 Unit Dimensions (hwd / cm) - 34.49 x 60.96 X 76.327 Unit Dimensions (in.) - 13.580 x 24.000 x 30.050 Unit Weight (lbs.) - 91.9 Unit Weight (kg) - 41.69 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 Mounting Details - Adjustable equipment mounting rail (10-32) Cable Entry/Exit - Sealed cut-out; compatible gland plates sold separately. FEATURES & SPECIFICATIONS Grounding Details - Cabinet Body Tools Necessary - Yes Built-in Cable Management - No Extra Wide - No Locking - Yes Lock Type - Key Pre-Installed Casters - No Outdoor Use - Yes Gasketed Door - Yes STANDARDS & COMPLIANCE Protection Rating - NEMA 4 Product Certifications - CAN/CSA-C22.2 No. 286 (Canada); UL 508A Product Compliance - EIA/ECA-310-E; NEMA 4; RoHS; REACH Also available in SRN4G6UDP,SRN4G9US,SRN4G9USDP ,SRN4G18UHD
SRN4G12U | UPC Code - 037332273116 Device Compatibility - Computer; DVR; Network Switch; PDU; Patch Panel; Server; UPS Rack Type - Enclosure PHYSICAL Color - Gray Material of Construction - Powder Coated Steel Rack Height - 12U Rack Depth - Mid Mounting Location - Wall Factory Preset Rack Depth (in.) - 20.00 Factory Preset Rack Depth (cm) - 50.8 Factory Preset Rack Depth (mm) - 508 Mounting Holes or Slots - Yes Maximum Device Depth (cm) - 58.42 Maximum Device Depth (in.) - 23 Maximum Device Depth (mm) - 584 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Shipping Form Factor - Factory Assembled Shipping Dimensions (hwd / in.) - 30.00 x 28.00 x 30.00 Shipping Dimensions (hwd / cm) - 76.20 x 71.12 x 76.20 Shipping Weight (lbs.) - 150.00 Shipping Weight (kg) - 68.04 Unit Dimensions (hwd / in.) - 24.080 x 24.000 x 25.160 Unit Dimensions (hwd / cm) - 61.163 x 61.163 X 63.910 Unit Dimensions (in.) - 24.080 x 24.000 x 25.160 Unit Weight (lbs.) - 96.3 Unit Weight (kg) - 43.68 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 Mounting Details - Adjustable equipment mounting rail (10-32) Cable Entry/Exit - Sealed cut-out; compatible gland plates sold separately. FEATURES & SPECIFICATIONS Grounding Details - Cabinet Body Tools Necessary - Yes Built-in Cable Management - No Extra Wide - No Locking - Yes Lock Type - Key Pre-Installed Casters - No Outdoor Use - Yes Gasketed Door - Yes STANDARDS & COMPLIANCE Protection Rating - NEMA 4 Product Certifications - CAN/CSA-C22.2 No. 286 (Canada); UL 508A Product Compliance - EIA/ECA-310-E; NEMA 4; RoHS; REACH. SRN4G12UHD,SRN4G12USDP
SRN4G6UDP | UPC Code - 037332273093 Device Compatibility - Computer; DVR; Network Switch; PDU; Patch Panel; Server; UPS Rack Type - Small Enclosure PHYSICAL Color - Gray Material of Construction - Powder Coated Steel Rack Height - 6U Rack Depth - Deep Mounting Location - Wall Factory Preset Rack Depth (in.) - 20.00 Factory Preset Rack Depth (cm) - 50.8 Factory Preset Rack Depth (mm) - 508 Mounting Holes or Slots - Yes Maximum Device Depth (cm) - 52.07 Maximum Device Depth (in.) - 20.5 Maximum Device Depth (mm) - 521 Minimum Device Depth (cm) - 7.62 Minimum Device Depth (in.) - 3 Minimum Device Depth (mm) - 76 Shipping Form Factor - Factory Assembled Shipping Dimensions (hwd / in.) - 21.50 x 27.00 x 28.00 Shipping Weight (kg) - 49.90 Unit Dimensions (hwd / in.) - 13.580 x 24.000 x 23.160 Unit Dimensions (hwd / cm) - 34.49 x 60.96 X 58.83 Unit Dimensions (in.) - 13.580 x 24.000 x 23.160 Unit Weight (lbs.) - 66.9 Unit Weight (kg) - 30.35 Weight Capacity - Stationary (kg) - 91 Weight Capacity - Stationary (lbs.) - 200 Number of Vertical Mounting Rails - 4 Mounting Details - Adjustable equipment mounting rail (10-32) Cable Entry/Exit - Sealed cut-out; compatible gland plates sold separately. FEATURES & SPECIFICATIONS Grounding Details - Cabinet Body Tools Necessary - Yes Built-in Cable Management - No Extra Wide - No Locking - Yes Lock Type - Key Pre-Installed Casters - No Outdoor Use - Yes Gasketed Door - Yes STANDARDS & COMPLIANCE Protection Rating - NEMA 4 Product Certifications - CAN/CSA-C22.2 No. 286 (Canada); UL 508A Product Compliance - EIA/ECA-310-E; NEMA 4; RoHS; REACH
ETN-ENC422442S | UPC Code - 037332278906 Device Compatibility - Server; Network Switch; Router; UPS; PDU; Patch Panel Rack Type - Enclosure PHYSICAL Color - Black Material of Construction - Powder Coated Steel Rack Height - 42U Rack Depth - Standard Factory Preset Rack Depth (in.) - 29.25 Factory Preset Rack Depth (cm) - 74.3 Factory Preset Rack Depth (mm) - 743 Maximum Device Depth (cm) - 91.44 Maximum Device Depth (in.) - 36 Maximum Device Depth (mm) - 914 Minimum Device Depth (cm) - 10.16 Minimum Device Depth (in.) - 4 Minimum Device Depth (mm) - 102 Shipping Form Factor - Factory Assembled Unit Dimensions (hwd / in.) - 81.000 x 24.000 x 42.000 Unit Weight (lbs.) - 300 Unit Weight (kg) - 136.08 Weight Capacity - Rolling (kg) - 907 Weight Capacity - Rolling (lbs.) - 2000 Weight Capacity - Stationary (kg) - 1,361 Weight Capacity - Stationary (lbs.) - 3000 Number of Vertical Mounting Rails - 4 FEATURES & SPECIFICATIONS Grounding Details - Front and back doors, rails, top and divider panels Built-in Cable Management - Yes Extra Wide - No Locking - Yes Lock Type - Key Pre-Installed Casters - Yes PDU Mounting Bracket - Yes Airflow Management - Brush strips; Rubber grommets; High flow perforated doors STANDARDS & COMPLIANCE Product Compliance - EIA/ECA-310-E; RoHS; Trade Agreements Act (TAA). Also available in ETN-ENC422448S,ETN-ENC423042S, ETN-ENC423048S ,ETN-ENC442442S, ETN-ENC442448S,ENC443042S, ETN-ENC443048S,ETN-ENC482442S, ETN-ENC482448S,ETN-ENC483042S, ETN-ENC483048S,ETN-ENC512442S, ETN-ENC512448S,ETN-ENC513042S, ETN-ENC513048S
SR12UB | UPC Code 037332157911 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Small Enclosure PHYSICAL Color Black Rack Height 12U Rack Depth Mid Factory Preset Rack Depth (in.) 28.31 Factory Preset Rack Depth (cm) 71.9 Factory Preset Rack Depth (mm) 719 Maximum Device Depth (cm) 82.55 Maximum Device Depth (in.) 32.5 Maximum Device Depth (mm) 826 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Cable Access Hole Measurement (inches) 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) 31.00 x 37.00 x 27.00 Shipping Dimensions (hwd / cm) 78.74 x 93.98 x 68.58 Shipping Weight (lbs.) 112.00 Shipping Weight (kg) 50.80 Unit Dimensions (hwd / in.) 25.100 x 23.600 x 33.500 Unit Dimensions (hwd / cm) 63.75 x 60 x 85.09 Unit Weight (lbs.) 105 Unit Weight (kg) 47.63 Weight Capacity - Rolling (kg) 454 Weight Capacity - Rolling (lbs.) 1000 Weight Capacity - Stationary (kg) 454 Weight Capacity - Stationary (lbs.) 1000 Number of Vertical Mounting Rails 4 Assembly Required Yes FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Pre-Installed Casters No STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; EIA/ECA-310-E; UKCA
SR12UBEXPNDKD | UPC Code 037332188472 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Open-Frame PHYSICAL Color Black Rack Height 12U Rack Depth Standard Maximum Device Depth (cm) 91.44 Maximum Device Depth (in.) 36 Maximum Device Depth (mm) 914 Minimum Device Depth (cm) 60.96 Minimum Device Depth (in.) 24 Minimum Device Depth (mm) 610 Shipping Dimensions (hwd / in.) 3.89 x 8.41 x 42.89 Shipping Dimensions (hwd / cm) 9.88 x 21.36 x 108.94 Shipping Weight (lbs.) 32.00 Shipping Weight (kg) 14.51 Unit Dimensions (hwd / in.) 25.600 x 20.370 x 35.940 Unit Dimensions (hwd / cm) 65.02 x 51.74 x 91.29 Unit Weight (lbs.) 45 Unit Weight (kg) 20.41 Weight Capacity - Stationary (kg) 454 Weight Capacity - Stationary (lbs.) 1000 Number of Vertical Mounting Rails 4 Assembly Required Yes FEATURES & SPECIFICATIONS Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E; UKCA
SR14UBDP | UPC Code 037332197917 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Small Enclosure PHYSICAL Color Black Rack Height 14U Rack Depth Standard Factory Preset Rack Depth (in.) 28.31 Factory Preset Rack Depth (cm) 71.9 Factory Preset Rack Depth (mm) 719 Maximum Device Depth (cm) 93.98 Maximum Device Depth (in.) 37 Maximum Device Depth (mm) 940 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Cable Access Hole Measurement (inches) 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) 33.55 x 25.87 x 45.98 Shipping Dimensions (hwd / cm) 85.22 x 65.71 x 116.79 Shipping Weight (lbs.) 156.00 Shipping Weight (kg) 70.76 Unit Dimensions (hwd / in.) 28.230 x 23.620 x 43.620 Unit Dimensions (hwd / cm) 71.70 x 60 x 110.80 Unit Weight (lbs.) 105 Unit Weight (kg) 47.63 Weight Capacity - Rolling (kg) 454 Weight Capacity - Rolling (lbs.) 1000 Weight Capacity - Stationary (kg) 454 Weight Capacity - Stationary (lbs.) 1000 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and back door frames Built-in Cable Management No Extra Wide No Locking No Pre-Installed Casters Yes Outdoor Use No STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; EIA/ECA-310-E; UKCA
SR18UB | UPC Code 037332178039 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Half-Height Enclosure PHYSICAL Color Black Rack Height 18U Rack Depth Mid Factory Preset Rack Depth (in.) 28.31 Factory Preset Rack Depth (cm) 71.9 Factory Preset Rack Depth (mm) 719 Maximum Device Depth (cm) 82.55 Maximum Device Depth (in.) 32.5 Maximum Device Depth (mm) 826 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Cable Access Hole Measurement (inches) 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) 41.00 x 24.00 x 34.00 Shipping Dimensions (hwd / cm) 104.14 x 60.96 x 86.36 Shipping Weight (lbs.) 125.00 Shipping Weight (kg) 56.70 Unit Dimensions (hwd / in.) 35.600 x 23.620 x 33.500 Unit Dimensions (hwd / cm) 90.42 x 60 x 85.09 Unit Weight (lbs.) 105 Unit Weight (kg) 47.63 Weight Capacity - Rolling (kg) 454 Weight Capacity - Rolling (lbs.) 1000 Weight Capacity - Stationary (kg) 454 Weight Capacity - Stationary (lbs.) 1000 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Built-in Cable Management Yes Extra Wide No Locking No Pre-Installed Casters Yes Outdoor Use No STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; EIA/ECA-310-E; UKCA
SR25UBEXP | UPC Code 037332178923 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Half-Height Enclosure PHYSICAL Color Black Rack Height 25U Rack Depth Standard Factory Preset Rack Depth (in.) 27.75 Factory Preset Rack Depth (cm) 70.5 Factory Preset Rack Depth (mm) 705 Maximum Device Depth (cm) 93.98 Maximum Device Depth (in.) 37 Maximum Device Depth (mm) 940 Minimum Device Depth (cm) 10.16 Minimum Device Depth (in.) 4 Minimum Device Depth (mm) 102 Shipping Dimensions (hwd / in.) 55.00 x 26.00 x 45.00 Shipping Dimensions (hwd / cm) 139.70 x 66.04 x 114.30 Shipping Weight (lbs.) 200.00 Shipping Weight (kg) 90.72 Unit Dimensions (hwd / in.) 49.000 x 23.630 x 43.000 Unit Dimensions (hwd / cm) 124.46 x 60 x 109.22 Unit Weight (lbs.) 163 Unit Weight (kg) 73.94 Weight Capacity - Rolling (kg) 1,021 Weight Capacity - Rolling (lbs.) 2250 Weight Capacity - Stationary (kg) 1,588 Weight Capacity - Stationary (lbs.) 3500 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Pre-Installed Casters Yes STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; CE (Europe); UKCA
SR2POST12 | UPC Code 037332188458 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Open-Frame PHYSICAL Color Black Rack Height 12U Rack Depth Standard EIA Mounting Rails M6 Cagenuts Maximum Device Depth (cm) 91.44 Maximum Device Depth (in.) 36 Maximum Device Depth (mm) 914 Shipping Dimensions (hwd / in.) 3.20 x 3.60 x 25.00 Shipping Dimensions (hwd / cm) 8.13 x 9.14 x 63.50 Shipping Weight (lbs.) 5.30 Shipping Weight (kg) 2.40 Unit Weight (lbs.) 4 Unit Weight (kg) 1.81 Weight Capacity - Stationary (kg) 50 Weight Capacity - Stationary (lbs.) 110 Number of Vertical Mounting Rails 2 Assembly Required Yes FEATURES & SPECIFICATIONS Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E
SR2POST12HD | UPC Code 037332258540 Device Compatibility Network Switch; PDU; Patch Panel; Server; UPS Rack Type Open-Frame PHYSICAL Color Black Rack Height 12U Rack Depth Shallow EIA Mounting Rails 12-24 threaded and numbered vertical mounting rails Maximum Device Depth (cm) 30.48 Maximum Device Depth (in.) 12.00 Maximum Device Depth (mm) 305 Shipping Dimensions (hwd / in.) 7.87 x 27.16 x 17.52 Shipping Weight (kg) 10.21 Unit Dimensions (hwd / in.) 24.610 x 20.690 x 11.700 Unit Dimensions (hwd / cm) 62.509 x 52.553 x 29.718 Unit Weight (lbs.) 22.00 Unit Weight (kg) 9.98 Weight Capacity - Stationary (kg) 159 Weight Capacity - Stationary (lbs.) 350 Number of Vertical Mounting Rails 2 Assembly Required Yes FEATURES & SPECIFICATIONS Built-in Cable Management No Extra Wide No Pre-Installed Casters No STANDARDS & COMPLIANCE Product Certifications CAN/CSA-C22.2 No. 62368-1 (Canada); UL 62368-1 Product Compliance RoHS Also available in SR2POST16HD
SR2POST13 | UPC Code 037332183644 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Open-Frame PHYSICAL Color Black Rack Height 13U Rack Depth Extra Deep EIA Mounting Rails 12-24 threaded and numbered vertical mounting rails Maximum Device Depth (cm) 121.92 Maximum Device Depth (in.) 48 Maximum Device Depth (mm) 1,219 Shipping Dimensions (hwd / in.) 4.53 x 6.50 x 30.71 Shipping Dimensions (hwd / cm) 11.51 x 16.51 x 78.00 Shipping Weight (lbs.) 24.00 Shipping Weight (kg) 10.89 Unit Dimensions (hwd / in.) 28.000 x 20.375 x 13.625 Unit Dimensions (hwd / cm) 71.12 x 51.56 x 12.07 Unit Weight (lbs.) 20 Unit Weight (kg) 9.07 Weight Capacity - Stationary (kg) 363 Weight Capacity - Stationary (lbs.) 800 Number of Vertical Mounting Rails 2 Assembly Required Yes FEATURES & SPECIFICATIONS Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E. Also available in SR2POST25 ,SR2POST
SR2POSTDP12HD | UPC Code 037332266569 Device Compatibility Network Switch; PDU; Patch Panel; Server; UPS Rack Type Open-Frame PHYSICAL Color Black Rack Height 45U Rack Depth Deep EIA Mounting Rails 12-24 threaded vertical mounting rails Mounting Holes or Slots Yes Maximum Device Depth (cm) 121.92 Maximum Device Depth (in.) 48 Maximum Device Depth (mm) 1,219 Unit Dimensions (hwd / in.) 85.830 x 20.300 x 13.500 Unit Dimensions (hwd / cm) 218.00 x 51.56 x 34.29 Unit Weight (lbs.) 92.00 Unit Weight (kg) 41.73 Weight Capacity - Stationary (kg) 907 Weight Capacity - Stationary (lbs.) 2000 Number of Vertical Mounting Rails 2 Mounting Details Pre-tapped #12-24 EIA mounting holes front and back for standard 19" rack-mounting, Toolless button keyhole mounting slots, strap/cable tie anchors, can be bolted to the floor Assembly Required Yes FEATURES & SPECIFICATIONS Built-in Cable Management Yes Extra Wide No Pre-Installed Casters No STANDARDS & COMPLIANCE Product Certifications IEC 60297-3 Product Compliance RoHS; EIA/ECA-310-E
SR2POSTDP24HD | UPC Code 037332266576 Device Compatibility Network Switch; PDU; Patch Panel; Server; UPS Rack Type Open-Frame PHYSICAL Color Black Rack Height 45U Rack Depth Deep EIA Mounting Rails 12-24 threaded vertical mounting rails Mounting Holes or Slots Yes Maximum Device Depth (cm) 121.92 Maximum Device Depth (in.) 48 Maximum Device Depth (mm) 1,219 Unit Dimensions (hwd / in.) 85.830 x 20.300 x 26.000 Unit Dimensions (hwd / cm) 218.00 x 51.56 x 60.96 Unit Weight (lbs.) 134.00 Unit Weight (kg) 60.78 Weight Capacity - Stationary (kg) 907 Weight Capacity - Stationary (lbs.) 2000 Number of Vertical Mounting Rails 2 Mounting Details Pre-tapped #12-24 EIA mounting holes front and back for standard 19" rack-mounting, Toolless button keyhole mounting slots, strap/cable tie anchors, can be bolted to the floor Assembly Required Yes FEATURES & SPECIFICATIONS Built-in Cable Management Yes Extra Wide No Pre-Installed Casters No STANDARDS & COMPLIANCE Product Certifications IEC 60297-3 Product Compliance RoHS; EIA/ECA-310-E
SR42BMDEXPNDNR3 | UPC Code 037332175687 Device Compatibility Patch Panel; Network Switch; UPS Rack Type Open-Frame PHYSICAL Color Black Rack Height 42U Rack Depth Mid Maximum Device Depth (cm) 78.74 Maximum Device Depth (in.) 31 Maximum Device Depth (mm) 787 Minimum Device Depth (cm) 10.16 Minimum Device Depth (in.) 4 Minimum Device Depth (mm) 102 Shipping Dimensions (hwd / in.) 85.00 x 26.00 x 37.80 Shipping Dimensions (hwd / cm) 215.90 x 66.04 x 96.01 Shipping Weight (lbs.) 130.00 Shipping Weight (kg) 58.97 Unit Dimensions (hwd / in.) 79.500 x 23.630 x 36.000 Unit Dimensions (hwd / cm) 201.93 x 60.02 x 91.44 Unit Weight (lbs.) 94 Unit Weight (kg) 42.64 Weight Capacity - Rolling (kg) 1,021 Weight Capacity - Rolling (lbs.) 2250 Weight Capacity - Stationary (kg) 1,588 Weight Capacity - Stationary (lbs.) 3500 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Built-in Cable Management No Extra Wide No Pre-Installed Casters Yes STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; CE (Europe); UKCA
UPC Code 037332239242 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Enclosure PHYSICAL Color Black Rack Height 42U Rack Depth Extra Deep Factory Preset Rack Depth (in.) 28.125 Factory Preset Rack Depth (cm) 71.4 Factory Preset Rack Depth (mm) 714 Maximum Device Depth (cm) 119.79 Maximum Device Depth (in.) 47.16 Maximum Device Depth (mm) 1,198 Minimum Device Depth (cm) 10.16 Minimum Device Depth (in.) 4 Minimum Device Depth (mm) 102 Shipping Dimensions (hwd / in.) 85.00 x 33.50 x 52.75 Shipping Dimensions (hwd / cm) 215.90 x 85.09 x 133.98 Shipping Weight (kg) 180.08 Unit Dimensions (hwd / in.) 78.500 x 23.630 x 50.910 Unit Dimensions (hwd / cm) 199.39 x 60.02 x 120.1 Unit Weight (lbs.) 315 Unit Weight (kg) 142.88 Weight Capacity - Rolling (kg) 1,021 Weight Capacity - Rolling (lbs.) 2250 Weight Capacity - Stationary (kg) 1,588 Weight Capacity - Stationary (lbs.) 3500 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Built-in Cable Management No Extra Wide No Pre-Installed Casters Yes STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; CE (Europe); UKCA
SR42UBMDEXP | UPC Code 037332175663 Device Compatibility Patch Panel; Network Switch; UPS Rack Type Enclosure PHYSICAL Color Black Rack Height 42U Rack Depth Mid Factory Preset Rack Depth (in.) 22.75 Factory Preset Rack Depth (cm) 57.8 Factory Preset Rack Depth (mm) 578 Maximum Device Depth (cm) 78.74 Maximum Device Depth (in.) 31 Maximum Device Depth (mm) 787 Minimum Device Depth (cm) 10.16 Minimum Device Depth (in.) 4 Minimum Device Depth (mm) 102 Shipping Dimensions (hwd / in.) 78.00 x 24.00 x 36.50 Shipping Dimensions (hwd / cm) 198.12 x 60.96 x 92.71 Shipping Weight (lbs.) 236.00 Shipping Weight (kg) 107.05 Unit Dimensions (hwd / in.) 78.500 x 23.630 x 36.000 Unit Dimensions (hwd / cm) 199.39 x 60.02 x 91.44 Unit Weight (lbs.) 186 Unit Weight (kg) 84.37 Weight Capacity - Rolling (kg) 1,021 Weight Capacity - Rolling (lbs.) 2250 Weight Capacity - Stationary (kg) 1,588 Weight Capacity - Stationary (lbs.) 3500 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Built-in Cable Management No Extra Wide No Pre-Installed Casters Yes STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; CE (Europe); UKCA. SR42UBEXP
SR45UBDP | UPC Code 037332174918 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Enclosure PHYSICAL Color Black Rack Height 45U Rack Depth Deep Factory Preset Rack Depth (in.) 28.125 Factory Preset Rack Depth (cm) 71.4 Factory Preset Rack Depth (mm) 714 Maximum Device Depth (cm) 106.68 Maximum Device Depth (in.) 42 Maximum Device Depth (mm) 1,067 Minimum Device Depth (cm) 10.16 Minimum Device Depth (in.) 4 Minimum Device Depth (mm) 102 Shipping Dimensions (hwd / in.) 90.30 x 26.00 x 53.00 Shipping Dimensions (hwd / cm) 229.36 x 66.04 x 134.62 Shipping Weight (lbs.) 390.00 Shipping Weight (kg) 176.90 Unit Dimensions (hwd / in.) 83.750 x 23.630 x 48.500 Unit Dimensions (hwd / cm) 212.725 x 60.02 x 123.19 Unit Weight (lbs.) 340 Unit Weight (kg) 154.22 Weight Capacity - Rolling (kg) 1,021 Weight Capacity - Rolling (lbs.) 2250 Weight Capacity - Stationary (kg) 1,588 Weight Capacity - Stationary (lbs.) 3500 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Built-in Cable Management Yes Extra Wide No Pre-Installed Casters Yes STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; CE (Europe); UKCA. SR45UBDP48,SR42UBDP48,SR48UBDP
SR45UBEXP | UPC Code 037332174772 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Enclosure PHYSICAL Color Black Rack Height 45U Rack Depth Standard Factory Preset Rack Depth (in.) 27.75 Factory Preset Rack Depth (cm) 70.5 Factory Preset Rack Depth (mm) 705 Maximum Device Depth (cm) 93.98 Maximum Device Depth (in.) 37 Maximum Device Depth (mm) 940 Minimum Device Depth (cm) 10.16 Minimum Device Depth (in.) 4 Minimum Device Depth (mm) 102 Shipping Dimensions (hwd / in.) 90.50 x 26.00 x 45.00 Shipping Dimensions (hwd / cm) 229.87 x 66.04 x 114.30 Shipping Weight (lbs.) 278.00 Shipping Weight (kg) 126.10 Unit Dimensions (hwd / in.) 83.750 x 23.630 x 43.000 Unit Dimensions (hwd / cm) 212.725 x 60.02 x 109.22 Unit Weight (lbs.) 223 Unit Weight (kg) 101.15 Weight Capacity - Rolling (kg) 1,021 Weight Capacity - Rolling (lbs.) 2250 Weight Capacity - Stationary (kg) 1,588 Weight Capacity - Stationary (lbs.) 3500 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Pre-Installed Casters Yes STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; CE (Europe)
SR45UBEXPND | UPC Code 037332174567 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Open-Frame PHYSICAL Color Black Rack Height 45U Rack Depth Standard Maximum Device Depth (cm) 93.98 Maximum Device Depth (in.) 37 Maximum Device Depth (mm) 940 Minimum Device Depth (cm) 10.16 Minimum Device Depth (in.) 4 Minimum Device Depth (mm) 102 Shipping Dimensions (hwd / in.) 90.50 x 26.00 x 45.00 Shipping Dimensions (hwd / cm) 229.87 x 66.04 x 114.30 Shipping Weight (lbs.) 197.00 Shipping Weight (kg) 89.36 Unit Dimensions (hwd / in.) 83.750 x 23.630 x 43.000 Unit Dimensions (hwd / cm) 212,725 x 60,02 x 109,22 Unit Weight (lbs.) 147 Unit Weight (kg) 66.68 Weight Capacity - Rolling (kg) 1,021 Weight Capacity - Rolling (lbs.) 2250 Weight Capacity - Stationary (kg) 1,588 Weight Capacity - Stationary (lbs.) 3500 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Pre-Installed Casters Yes STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; CE (Europe). Also available SR45UBMDEXPND,SR45UBEXPNDNR3 , SR42UBMDEXPND
SR48UBEXP | UPC Code 037332151001 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Enclosure PHYSICAL Color Black Rack Height 48U Rack Depth Standard Factory Preset Rack Depth (in.) 27.75 Factory Preset Rack Depth (cm) 70.5 Factory Preset Rack Depth (mm) 705 Maximum Device Depth (cm) 93.98 Maximum Device Depth (in.) 37 Maximum Device Depth (mm) 940 Minimum Device Depth (cm) 10.16 Minimum Device Depth (in.) 4 Minimum Device Depth (mm) 102 Shipping Dimensions (hwd / in.) 95.00 x 26.00 x 45.00 Shipping Dimensions (hwd / cm) 241.30 x 66.04 x 114.30 Shipping Weight (lbs.) 267.00 Shipping Weight (kg) 121.11 Unit Dimensions (hwd / in.) 89.000 x 23.630 x 43.000 Unit Dimensions (hwd / cm) 226.06 x 60.02 x 109.22 Unit Weight (lbs.) 211 Unit Weight (kg) 95.71 Weight Capacity - Rolling (kg) 1,021 Weight Capacity - Rolling (lbs.) 2250 Weight Capacity - Stationary (kg) 1,588 Weight Capacity - Stationary (lbs.) 3500 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Pre-Installed Casters Yes STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; CE (Europe); UKCA
SR4POST | UPC Code 037332127570 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Open-Frame PHYSICAL Color Black Rack Height 45U Rack Depth Standard Maximum Device Depth (cm) 91.44 Maximum Device Depth (in.) 36 Maximum Device Depth (mm) 914 Minimum Device Depth (cm) 55.88 Minimum Device Depth (in.) 22 Minimum Device Depth (mm) 559 Shipping Dimensions (hwd / in.) 4.53 x 6.50 x 87.99 Shipping Dimensions (hwd / cm) 11.51 x 16.51 x 223.49 Shipping Weight (lbs.) 60.00 Shipping Weight (kg) 27.22 Unit Dimensions (hwd / in.) 84.300 x 20.200 x 39.300 Unit Dimensions (hwd / cm) 214.122 x 51.31 x 55.88 - 91.44 Unit Weight (lbs.) 54 Unit Weight (kg) 24.49 Weight Capacity - Stationary (kg) 454 Weight Capacity - Stationary (lbs.) 1000 Number of Vertical Mounting Rails 4 Assembly Required Yes FEATURES & SPECIFICATIONS Grounding Details Includes screws, washers, and bolts to secure user-supplied grounding wire to front or back frames Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E Also available in SR4POST1224,SR4POST13, SR4POST25,SR4POST48HD, SR4POST50HD,SR4POST52HD, SR4POST58HD
SR50UB | UPC Code 037332260772 Device Compatibility Network Switch; PDU; Patch Panel; Router; Server; UPS Rack Type Enclosure PHYSICAL Color Black Rack Height 50U Rack Depth Standard Factory Preset Rack Depth (in.) 27.75 Factory Preset Rack Depth (cm) 70.5 Factory Preset Rack Depth (mm) 705 Maximum Device Depth (cm) 93.98 Maximum Device Depth (in.) 37 Maximum Device Depth (mm) 940 Minimum Device Depth (cm) 10.16 Minimum Device Depth (in.) 4 Minimum Device Depth (mm) 102 Shipping Dimensions (hwd / in.) 97.70 x 25.75 x 45.50 Shipping Weight (kg) 181.85 Unit Dimensions (hwd / in.) 92.420 x 23.622 x 43.000 Unit Dimensions (hwd / cm) 234.75 x 60.00 x 109.22 Unit Weight (lbs.) 347.200 Unit Weight (kg) 157.49 Weight Capacity - Rolling (kg) 1,021 Weight Capacity - Rolling (lbs.) 2250 Weight Capacity - Stationary (kg) 1,588 Weight Capacity - Stationary (lbs.) 3500 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and back door frames Built-in Cable Management Yes Extra Wide No Pre-Installed Casters Yes STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; CE (Europe); UKCA. Also available in SR52UB,SR52UBDP, SR48UBDPWD
SRH42UW | UPC Code 037332290137 Device Compatibility AI Server (extra deep); Server Rack Type Enclosure PHYSICAL Color White Material of Construction Steel Rack Height 42U Rack Depth Standard Maximum Device Depth (cm) 104.14 Maximum Device Depth (in.) 41 Maximum Device Depth (mm) 1,041 Shipping Form Factor Factory Assembled Unit Dimensions (hwd / in.) 79.640 x 23.640 x 44.090 Unit Dimensions (hwd / cm) 199.39 x 60.02 x 109.22 Unit Weight (lbs.) 431 Unit Weight (kg) 195.50 Weight Capacity - Rolling (kg) 1,588 Weight Capacity - Rolling (lbs.) 3500 Weight Capacity - Stationary (kg) 2,268 Weight Capacity - Stationary (lbs.) 5000 Number of Vertical Mounting Rails 4 Assembly Required No FEATURES & SPECIFICATIONS Grounding Details Front and rear door frames Built-in Cable Management No Leveling Feet Yes Extra Wide No Locking Yes Pre-Installed Casters Yes Outdoor Use No STANDARDS & COMPLIANCE Product Certifications UL 62368-1; UL 2416 Product Compliance CE (Europe); RoHS; UKCA Also available in SRH42UWDP,SRH42UWDP54, SRH42UWDP54WD8,SRH42UWDPWD8, SRH42UWWD8,SRH45UW, SRH45UWDP,SRH45UWDP54, SRH45UWDP54WD8,SRH45UWDPWD8, SRH45UWWD8 SRH48UW,SRH48UWDP, SRH48UWDP54,SRH48UWDP54WD8, SRH48UWDPWD8
SRQP42UB | UPC Code 037332204059 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Enclosure PHYSICAL Color Black Rack Height 42U Rack Depth Standard Factory Preset Rack Depth (in.) 27.75 Factory Preset Rack Depth (cm) 70.5 Factory Preset Rack Depth (mm) 705 Maximum Device Depth (cm) 93.98 Maximum Device Depth (in.) 37 Maximum Device Depth (mm) 940 Minimum Device Depth (cm) 10.16 Minimum Device Depth (in.) 4 Minimum Device Depth (mm) 102 Shipping Dimensions (hwd / in.) 83.46 x 25.98 x 58.66 Shipping Dimensions (hwd / cm) 211.99 x 65.99 x 149.00 Shipping Weight (lbs.) 573.20 Shipping Weight (kg) 260.00 Unit Dimensions (hwd / in.) 78.500 x 23.630 x 56.340 Unit Dimensions (hwd / cm) 199.34 x 59.99 x 109.22 Unit Weight (lbs.) 523.00 Unit Weight (kg) 237.23 Weight Capacity - Rolling (kg) 907 Weight Capacity - Rolling (lbs.) 2000 Weight Capacity - Stationary (kg) 1,089 Weight Capacity - Stationary (lbs.) 2400 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and back door frames Built-in Cable Management Yes Extra Wide No Pre-Installed Casters Yes STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; CE (Europe); UKCA. Also available in SRW12U13
SRW12U13G | UPC Code 037332187314 Device Compatibility Patch Panel Rack Type Small Enclosure PHYSICAL Color Black Rack Height 12U Rack Depth Shallow Maximum Device Depth (cm) 32.38 Maximum Device Depth (in.) 12.75 Maximum Device Depth (mm) 324 Cable Access Hole Measurement (inches) 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) 15.75 x 25.60 x 27.56 Shipping Dimensions (hwd / cm) 40.00 x 65.02 x 70.00 Shipping Weight (lbs.) 38.00 Shipping Weight (kg) 17.24 Unit Dimensions (hwd / in.) 25.080 x 23.620 x 13.000 Unit Dimensions (hwd / cm) 63.7 x 59.99 x 33.02 Unit Weight (lbs.) 38 Unit Weight (kg) 17.24 Weight Capacity - Stationary (kg) 91 Weight Capacity - Stationary (lbs.) 200 Number of Vertical Mounting Rails 2 FEATURES & SPECIFICATIONS Grounding Details Front door frame Pre-Installed Casters No STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; EIA/ECA-310-E
SRW12US33 | UPC Code 037332156044 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Small Enclosure PHYSICAL Color Black Rack Height 12U Rack Depth Mid Factory Preset Rack Depth (in.) 25.99 Factory Preset Rack Depth (cm) 66.0 Factory Preset Rack Depth (mm) 660 Maximum Device Depth (cm) 82.55 Maximum Device Depth (in.) 32.5 Maximum Device Depth (mm) 826 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Cable Access Hole Measurement (inches) 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) 30.20 x 26.10 x 36.06 Shipping Dimensions (hwd / cm) 76.71 x 66.29 x 91.59 Shipping Weight (lbs.) 110.60 Shipping Weight (kg) 50.17 Unit Dimensions (hwd / in.) 25.100 x 23.600 x 33.500 Unit Dimensions (hwd / cm) 63.5 x 60 x 85.09 Unit Weight (lbs.) 100 Unit Weight (kg) 45.36 Weight Capacity - Stationary (kg) 113 Weight Capacity - Stationary (lbs.) 250 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E; UKCA. Also available in SRWO8U22DP
SRW12US33G | UPC Code 037332187352 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Small Enclosure PHYSICAL Color Black Rack Height 12U Rack Depth Mid Factory Preset Rack Depth (in.) 25.99 Factory Preset Rack Depth (cm) 66.0 Factory Preset Rack Depth (mm) 660 Maximum Device Depth (cm) 82.55 Maximum Device Depth (in.) 32.5 Maximum Device Depth (mm) 826 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Cable Access Hole Measurement (inches) 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) 30.20 x 26.10 x 36.06 Shipping Dimensions (hwd / cm) 76.71 x 66.29 x 91.59 Shipping Weight (lbs.) 118.00 Shipping Weight (kg) 53.52 Unit Dimensions (hwd / in.) 25.100 x 23.600 x 33.500 Unit Dimensions (hwd / cm) 63.5 x 60 x 85.09 Unit Weight (lbs.) 94.5 Unit Weight (kg) 42.86 Weight Capacity - Stationary (kg) 113 Weight Capacity - Stationary (lbs.) 250 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Built-in Cable Management No Extra Wide No Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E; UKCA
SRW12USDP | UPC Code 037332189691 Device Compatibility Patch Panel; Network Switch; UPS Rack Type Small Enclosure PHYSICAL Color Black Rack Height 12U Rack Depth Shallow Factory Preset Rack Depth (in.) 10.42 Factory Preset Rack Depth (cm) 26.5 Factory Preset Rack Depth (mm) 265 Maximum Device Depth (cm) 62.23 Maximum Device Depth (in.) 24.5 Maximum Device Depth (mm) 622 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Cable Access Hole Measurement (inches) 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) 30.00 x 30.00 x 31.00 Shipping Dimensions (hwd / cm) 76.20 x 76.20 x 78.74 Shipping Weight (lbs.) 92.00 Shipping Weight (kg) 41.73 Unit Dimensions (hwd / in.) 25.060 x 23.630 x 25.500 Unit Dimensions (hwd / cm) 63.65 x 60 x 64.77 Unit Weight (lbs.) 63.5 Unit Weight (kg) 28.80 Weight Capacity - Stationary (kg) 91 Weight Capacity - Stationary (lbs.) 200 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E; UKCA
SRW12USDPG | UPC Code 037332189721 Device Compatibility Patch Panel; Network Switch; UPS Rack Type Small Enclosure PHYSICAL Color Black Rack Height 12U Rack Depth Shallow Factory Preset Rack Depth (in.) 10.42 Factory Preset Rack Depth (cm) 26.5 Factory Preset Rack Depth (mm) 265 Maximum Device Depth (cm) 62.23 Maximum Device Depth (in.) 24.5 Maximum Device Depth (mm) 622 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Shipping Dimensions (hwd / in.) 29.33 x 28.15 x 29.92 Shipping Dimensions (hwd / cm) 74.50 x 71.50 x 76.00 Shipping Weight (lbs.) 92.00 Shipping Weight (kg) 41.73 Unit Dimensions (hwd / in.) 25.060 x 23.630 x 25.500 Unit Dimensions (hwd / cm) 63.65 x 60.02 x 64.77 Unit Weight (lbs.) 64 Unit Weight (kg) 29.03 Weight Capacity - Stationary (kg) 91 Weight Capacity - Stationary (lbs.) 200 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E; UKCA
SRW12USG | UPC Code 037332154859 Device Compatibility Patch Panel; Network Switch; UPS Rack Type Small Enclosure PHYSICAL Color Black Rack Height 12U Rack Depth Shallow Factory Preset Rack Depth (in.) 10.42 Factory Preset Rack Depth (cm) 26.5 Factory Preset Rack Depth (mm) 265 Maximum Device Depth (cm) 52.07 Maximum Device Depth (in.) 20.5 Maximum Device Depth (mm) 521 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Shipping Dimensions (hwd / in.) 26.00 x 24.30 x 28.00 Shipping Dimensions (hwd / cm) 66.04 x 61.72 x 71.12 Shipping Weight (lbs.) 66.00 Shipping Weight (kg) 29.94 Unit Dimensions (hwd / in.) 24.630 x 23.500 x 21.630 Unit Dimensions (hwd / cm) 63,5 x 60 x 54,86 Unit Weight (lbs.) 60 Unit Weight (kg) 27.22 Weight Capacity - Stationary (kg) 91 Weight Capacity - Stationary (lbs.) 200 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E; UKCA
SRW18UHD | UPC Code 037332183316 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Half-Height Enclosure PHYSICAL Color Black Rack Height 18U Rack Depth Mid EIA Mounting Rails Square holes / 12-24 threaded holes Maximum Device Depth (cm) 82.55 Maximum Device Depth (in.) 32.5 Maximum Device Depth (mm) 826 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Shipping Dimensions (hwd / in.) 42.72 x 25.79 x 37.20 Shipping Dimensions (hwd / cm) 108.51 x 65.51 x 94.49 Shipping Weight (lbs.) 78.90 Shipping Weight (kg) 35.79 Unit Dimensions (hwd / in.) 36.960 x 24.770 x 36.220 Unit Dimensions (hwd / cm) 93.88 x 92 x 62.92 Unit Weight (lbs.) 119.9 Unit Weight (kg) 54.39 Weight Capacity - Stationary (kg) 227 Weight Capacity - Stationary (lbs.) 500 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Built-in Cable Management No Extra Wide No Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E
SRW18US | UPC Code 037332154835 Device Compatibility Patch Panel; Network Switch; UPS Rack Type Half-Height Enclosure PHYSICAL Color Black Rack Height 18U Rack Depth Shallow Factory Preset Rack Depth (in.) 9.84 Factory Preset Rack Depth (cm) 25.0 Factory Preset Rack Depth (mm) 250 Maximum Device Depth (cm) 52.07 Maximum Device Depth (in.) 20.5 Maximum Device Depth (mm) 521 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Cable Access Hole Measurement (inches) 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) 40.71 x 26.10 x 24.13 Shipping Dimensions (hwd / cm) 103.40 x 66.29 x 61.29 Shipping Weight (lbs.) 112.00 Shipping Weight (kg) 50.80 Unit Dimensions (hwd / in.) 35.600 x 23.600 x 21.600 Unit Dimensions (hwd / cm) 90.42 x 59.9 x 54.86 Unit Weight (lbs.) 96 Unit Weight (kg) 43.54 Weight Capacity - Stationary (kg) 113 Weight Capacity - Stationary (lbs.) 250 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E; UKCA
SRW18US13 | UPC Code 037332177964 Device Compatibility Patch Panel Rack Type Half-Height Enclosure PHYSICAL Color Black Rack Height 18U Rack Depth Shallow Maximum Device Depth (cm) 32.38 Maximum Device Depth (in.) 12.75 Maximum Device Depth (mm) 324 Cable Access Hole Measurement (inches) 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) 15.55 x 26.10 x 40.71 Shipping Dimensions (hwd / cm) 39.50 x 66.29 x 103.40 Shipping Weight (lbs.) 79.00 Shipping Weight (kg) 35.83 Unit Dimensions (hwd / in.) 35.600 x 23.620 x 13.000 Unit Dimensions (hwd / cm) 90.42 x 59.9 x 33.02 Unit Weight (lbs.) 83.77 Unit Weight (kg) 38.00 Weight Capacity - Stationary (kg) 113 Weight Capacity - Stationary (lbs.) 250 Number of Vertical Mounting Rails 2 FEATURES & SPECIFICATIONS Grounding Details Front door frame Pre-Installed Casters No STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; EIA/ECA-310-E; UKCA. Also available in SRW18US13G
SRW18USG | UPC Code 037332187376 Device Compatibility Patch Panel; Network Switch; UPS Rack Type Half-Height Enclosure PHYSICAL Color Black Rack Height 18U Rack Depth Shallow Factory Preset Rack Depth (in.) 10.42 Factory Preset Rack Depth (cm) 26.5 Factory Preset Rack Depth (mm) 265 Maximum Device Depth (cm) 52.07 Maximum Device Depth (in.) 20.5 Maximum Device Depth (mm) 521 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Shipping Dimensions (hwd / in.) 41.00 x 27.00 x 24.00 Shipping Dimensions (hwd / cm) 104.14 x 68.58 x 60.96 Shipping Weight (lbs.) 117.00 Shipping Weight (kg) 53.07 Unit Dimensions (hwd / in.) 35.600 x 23.600 x 21.600 Unit Dimensions (hwd / cm) 90.42 x 60 x 54.86 Unit Weight (lbs.) 96 Unit Weight (kg) 43.54 Weight Capacity - Stationary (kg) 113 Weight Capacity - Stationary (lbs.) 250 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E; UKCA
SRW26US | UPC Code 037332154842 Device Compatibility Patch Panel; Network Switch; UPS Rack Type Half-Height Enclosure PHYSICAL Color Black Rack Height 26U Rack Depth Shallow Factory Preset Rack Depth (in.) 11.42 Factory Preset Rack Depth (cm) 29.0 Factory Preset Rack Depth (mm) 290 Maximum Device Depth (cm) 52.07 Maximum Device Depth (in.) 20.5 Maximum Device Depth (mm) 521 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Cable Access Hole Measurement (inches) 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) 22.00 x 24.00 x 55.00 Shipping Dimensions (hwd / cm) 55.88 x 60.96 x 139.70 Shipping Weight (lbs.) 142.00 Shipping Weight (kg) 64.41 Unit Dimensions (hwd / in.) 49.700 x 23.600 x 21.600 Unit Dimensions (hwd / cm) 126.24 x 60 x 54.86 Unit Weight (lbs.) 125 Unit Weight (kg) 56.70 Weight Capacity - Stationary (kg) 113 Weight Capacity - Stationary (lbs.) 250 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E; UKCA
SRW4USM | UPC Code 037332282699 Device Compatibility PDU; Server Rack Type Small Enclosure PHYSICAL Color Black Rack Height 4U Rack Depth Shallow Maximum Device Depth (cm) 74.68 Maximum Device Depth (in.) 29.4 Maximum Device Depth (mm) 747 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Unit Dimensions (hwd / in.) 25.539 x 37.946 x 11.000 Unit Dimensions (hwd / cm) 64.859 x 96.401 x 27.940 Weight Capacity - Stationary (kg) 91 Weight Capacity - Stationary (lbs.) 200 Number of Vertical Mounting Rails 4 Assembly Required No FEATURES & SPECIFICATIONS Grounding Details Front and back door frames IP20 Rated Yes Built-in Cable Management No Extra Wide No Locking No Pre-Installed Casters No Outdoor Use No STANDARDS & COMPLIANCE Product Compliance EIA/ECA-310-E; RoHS. Also available in SRW26USG,SRW26USDPG , SRW26USDP,SRW18USDPG,SRW18USDP
SRW6USM | UPC Code 037332282705 Device Compatibility PDU; Server Rack Type Small Enclosure PHYSICAL Color Black Rack Height 6U Rack Depth Shallow Maximum Device Depth (cm) 74.68 Maximum Device Depth (in.) 29.4 Maximum Device Depth (mm) 747 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Unit Dimensions (hwd / in.) 26.600 x 39.050 x 13.900 Unit Dimensions (hwd / cm) 67.564 x 99.197 x 35.306 Unit Weight (lbs.) 99.8 Unit Weight (kg) 45.27 Weight Capacity - Stationary (kg) 113 Weight Capacity - Stationary (lbs.) 250 Number of Vertical Mounting Rails 4 Assembly Required No FEATURES & SPECIFICATIONS Grounding Details Front and back door frames IP20 Rated Yes Built-in Cable Management No Extra Wide No Locking No Pre-Installed Casters No Outdoor Use No STANDARDS & COMPLIANCE Product Compliance EIA/ECA-310-E; RoHS
SRW9UDPW | UPC Code 037332256065 Device Compatibility Patch Panel; Network Switch; UPS Rack Type Small Enclosure PHYSICAL Color White Rack Height 9U Rack Depth Shallow Maximum Device Depth (cm) 52.07 Maximum Device Depth (in.) 20.5 Maximum Device Depth (mm) 521 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Cable Access Hole Measurement (inches) 9.812 x 2.35 (l x w) Shipping Dimensions (hwd / in.) 24.41 x 28.75 x 26.57 Shipping Weight (kg) 22.23 Unit Dimensions (hwd / in.) 19.830 x 23.620 x 21.710 Unit Dimensions (hwd / cm) 50.37 x 59.99 x 55.14 Unit Weight (lbs.) 51.8 Unit Weight (kg) 23.50 Weight Capacity - Stationary (kg) 91 Weight Capacity - Stationary (lbs.) 200 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Built-in Cable Management No Extra Wide No Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E
SRW9USM | UPC Code 037332282712 Device Compatibility PDU; Server Rack Type Small Enclosure PHYSICAL Color Black Rack Height 9U Rack Depth Shallow Maximum Device Depth (cm) 74.68 Maximum Device Depth (in.) 29.4 Maximum Device Depth (mm) 747 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Unit Dimensions (hwd / in.) 25.590 x 38.976 x 20.101 Unit Dimensions (hwd / cm) 64.899 x 99.002 x 51.056 Unit Weight (lbs.) 110 Unit Weight (kg) 49.90 Weight Capacity - Stationary (kg) 113 Weight Capacity - Stationary (lbs.) 250 Number of Vertical Mounting Rails 4 Assembly Required No FEATURES & SPECIFICATIONS Grounding Details Front and back door frames IP20 Rated Yes Built-in Cable Management No Extra Wide No Locking No Pre-Installed Casters No Outdoor Use No STANDARDS & COMPLIANCE Product Compliance EIA/ECA-310-E; RoHS
Tripp Lite series SmartRack 2U Vertical Wall-Mount Rack Bracket | 19-inch wall-mount rack with maximum load capacity of 175 lbs (79.4 kgs) Provides open, unrestricted access to equipment and cabling Made from cold-rolled steel with black powder-coated finish Equipment-mounting hardware included Compatible with most EIA-standard 19 in. 2-post rack equipment 5-year limited warranty Also available in SRWALLBRKT6U,SRWALLBRKT4U
Tripp Lite series SmartRack 12U Low-Profile Vertical-Mount Wall-Mount Small Server Rack Enclosure | Device Compatibility Network Switch; Patch Panel; Server Rack Type Small Enclosure PHYSICAL Color Black Rack Height 12U Maximum load capacity of 400 lbs (181.4 kgs) Locking steel cabinet vented to keep equipment cool Secures 8U of 19 in. rack equipment up to 35 in. deep Includes additional 4U of space for patch panels Modular design for easy disassembly and assembly 5-year limited warranty Also available in SRWF16U38
Tripp Lite series SmartRack 2U Low-Profile Vertical-Mount Server-Depth Wall-Mount Rack Enclosure Cabinet | Color Black Wall-mount cabinet secures and organizes 2U of 19-inch rack equipment in network wiring closets and other locations with limited floor space. Houses equipment up to 36 inches deep, but extends less than 5 inches from wall. Maximum load capacity of 150 lbs (68 kgs) Locking steel cabinet vented to keep equipment cool Secures 2U of 19 in. rack equipment up to 36 in. deep Includes additional 1U of space for patch panels Ships fully assembled for quick installation 5-year limited warranty. Also available in SRWF2U
Tripp Lite series SmartRack 5U Low-Profile Vertical-Mount Server-Depth Wall-Mount Rack Enclosure Cabinet | Wall-mount cabinet secures and organizes 5U of 19-inch rack equipment in locations with limited floor space. Houses servers and other equipment up to 36 inches deep, but extends less than 10 inches from wall. Maximum load capacity of 150 lbs (68 kgs) Locking steel cabinet vented to keep equipment cool Secures 5U of 19 in. rack equipment up to 36 in. deep Includes additional 2U of space for patch panels Ships fully assembled for quick installation 5-year limited warranty Also available in SRWF6U SRWF5U,SRWF4U36 SRWF4U
SRWF6U36 | UPC Code 037332190642 Device Compatibility Patch Panel; Network Switch; Server Rack Type Small Enclosure PHYSICAL Color Black Rack Height 6U Rack Depth Standard Maximum Device Depth (cm) 91.44 Maximum Device Depth (in.) 36 Maximum Device Depth (mm) 914 Shipping Dimensions (hwd / in.) 18.00 x 32.00 x 49.00 Shipping Dimensions (hwd / cm) 45.72 x 81.28 x 124.46 Shipping Weight (lbs.) 87.00 Shipping Weight (kg) 39.46 Unit Dimensions (hwd / in.) 43.000 x 25.600 x 11.500 Unit Dimensions (hwd / cm) 109,83 x 67,82 x 30,40 Unit Weight (lbs.) 88.20 Unit Weight (kg) 40.01 Weight Capacity - Stationary (kg) 68 Weight Capacity - Stationary (lbs.) 150 Number of Vertical Mounting Rails 2 FEATURES & SPECIFICATIONS Built-in Cable Management No Extra Wide No Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E
SRWF6UMOD | UPC Code 037332250629 Device Compatibility Patch Panel; Network Switch; Server Rack Type Small Enclosure PHYSICAL Color Black Rack Height 3U Rack Depth Shallow Maximum Device Depth (cm) 41.91 Maximum Device Depth (in.) 16.5 Maximum Device Depth (mm) 419 Shipping Dimensions (hwd / in.) 10.50 x 23.00 x 38.10 Shipping Weight (kg) 16.96 Unit Dimensions (hwd / in.) 35.560 x 20.000 x 7.070 Unit Dimensions (hwd / cm) 90.32 x 50.80 x 17.96 Unit Weight (lbs.) 30.90 Unit Weight (kg) 14.02 Weight Capacity - Stationary (kg) 68 Weight Capacity - Stationary (lbs.) 150 Number of Vertical Mounting Rails 2 FEATURES & SPECIFICATIONS Built-in Cable Management No Extra Wide No Locking No Pre-Installed Casters No Outdoor Use No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E
12U Wall-Mount Bracket with Shelf for Small Switches and Patch Panels, Hinged | Accessory Type Mounting Bracket; Rack-Mount Shelf Kit Accessory Class Rack AccessoriesHighlights Ideal for home office or smallbusiness with no floor space forfull-size rack cabinet Steel construction with smooth laser-cut edges that won't damage cable jackets Supports universal mounting for left- or right-hinging to alloweasy cable access Keyhole mounting slots spaced16 in. apart to match standardwall-stud placement Included shelf holds non-rackitems like routers and towerUPS systems Also available in SRWO8UBRKTSHELF
SRWO12US | UPC Code 037332156761 Device Compatibility Patch Panel; Network Switch Rack Type Open-Frame PHYSICAL Color Black Rack Height 12U Rack Depth Shallow Maximum Device Depth (cm) 45.72 Maximum Device Depth (in.) 18 Maximum Device Depth (mm) 457 Shipping Dimensions (hwd / in.) 4.10 x 24.40 x 20.10 Shipping Dimensions (hwd / cm) 10.41 x 61.98 x 51.05 Shipping Weight (lbs.) 16.00 Shipping Weight (kg) 7.26 Unit Dimensions (hwd / in.) 31.040 x 19.760 x 20.350 Unit Dimensions (hwd / cm) 78.04 x 50.19 x 51.69 Unit Weight (lbs.) 15 Unit Weight (kg) 6.80 Weight Capacity - Stationary (kg) 68 Weight Capacity - Stationary (lbs.) 150 Number of Vertical Mounting Rails 2 Assembly Required Yes FEATURES & SPECIFICATIONS Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E
SmartRack 12U Wall-Mount 2-Post Open Frame Rack, Hinged Front, Heavy Duty | Rack Type Open-Frame Wall-mount open frame rack stores 12U of 19-inch rack equipment up to 22 inches deep and swings open for maximum accessibility. 12U 2-post rack accommodates 19 in. rack equipment up to 22 in. deep Hinged front provides easy rear access to cables and equipment Keyhole mounting slots are spaced 16 in. apart to match standard wall stud placement Maximum load capacity is 150 lb. Assembly hardware is included 5-year limited warranty Also available in SRWO16US, SRWO12UHD
Tripp Lite series SmartRack 2U Low-Profile Vertical-Mount Vented Wall-Mount Mini Rack Enclosure, Black | Rack Type Small Enclosure Wall-mount cabinet secures and organizes 2U of rack equipment in confined spaces, such as classrooms and back offices. Low-profile cabinet extends less than 5 in. from wall to save space in small areas Heavy-duty cold-rolled steel construction with maximum load capacity of 75 lb. Vented design maximizes airflow to protect equipment against excessive heat Keyhole mounting slots spaced 16 in. apart to match standard wall-stud placement Includes equipment-mounting hardware for convenient installation 5-year limited warranty Also available in SRWO4UBRKT
SRWO4UBRKTSHELF | UPC Code 037332262950 Device Compatibility Network Switch; Patch Panel; Router Rack Type Bracket Accessory Type Mounting Accessories PHYSICAL Color Black Rack Height 4U Rack Depth Shallow Maximum Device Depth (cm) 38.10 Maximum Device Depth (in.) 15 Maximum Device Depth (mm) 381 Unit Dimensions (hwd / in.) 10.680 x 19.860 x 15.000 Unit Dimensions (hwd / cm) 27.127 x 50.444 x 38.100 Unit Weight (lbs.) 19.410 Unit Weight (kg) 8.80 Weight Capacity - Stationary (kg) 68 Weight Capacity - Stationary (lbs.) 150 Number of Vertical Mounting Rails 2 Assembly Required Yes FEATURES & SPECIFICATIONS Built-in Cable Management No Extra Wide No Pre-Installed Casters No STANDARDS & COMPLIANCE Product Certifications IEC 60297-3 Product Compliance EIA/ECA-310-E; REACH; RoHS
Tripp Lite series SmartRack 8U/12U/22U Expandable Flat-Pack Low-Profile Switch-Depth Wall-Mount 2-Post Open Frame Rack | Rack Type Open-Frame Expandable open-frame rack stores 8U, 12U or 22U of 19-inch rack equipment up to 18 inches deep in locations with limited floor space where a locked enclosure is not required. Allows easy access to equipment and cabling. Maximum load capacity of 150 lbs (68 kgs) Configures to 8U, 12U or 22U of rack space Allows easy access to equipment and cabling Stores 19 in. rack equipment up to 18 in. deep Simple to assemble and mount 5-year limited warranty Also available in SRWO8U22MD
SRWO8U22SD | UPC Code 037332187406 Device Compatibility Patch Panel Rack Type Open-Frame PHYSICAL Color Black Rack Height 22U Rack Depth Shallow Maximum Device Depth (cm) 14.60 Maximum Device Depth (in.) 5.75 Maximum Device Depth (mm) 146 Maximum Weight Capacity (lbs.) 150 Maximum Weight Capacity (kg) 68 Shipping Dimensions (hwd / in.) 3.95 x 21.25 x 21.46 Shipping Dimensions (hwd / cm) 10.03 x 53.98 x 54.51 Shipping Weight (lbs.) 14.00 Shipping Weight (kg) 6.35 Unit Dimensions (hwd / in.) 0.000 x 20.110 x 6.000 Unit Dimensions (hwd / cm) 45.22 (8U), 63 (12U), 107.45 (22U) x 51.08 x 45.24 Unit Weight (lbs.) 14.1 Unit Weight (kg) 6.40 Unit Weight Details Weight varies depending on configuration 8U = 7.69lbs, 12U = 8.7lbs, 22U = 11.53lbs Number of Vertical Mounting Rails 2 Assembly Required Yes FEATURES & SPECIFICATIONS Pre-Installed Casters No STANDARDS & COMPLIANCE Product Compliance RoHS; EIA/ECA-310-E
SRWO8UBRKT | UPC Code 037332205629 Device Compatibility Patch Panel Rack Type Bracket Accessory Type Mounting Accessories PHYSICAL Color Black Rack Height 8U Rack Depth Shallow Maximum Device Depth (cm) 38.10 Maximum Device Depth (in.) 15 Maximum Device Depth (mm) 381 Shipping Dimensions (hwd / in.) 3.94 x 21.46 x 17.13 Shipping Dimensions (hwd / cm) 10.01 x 54.51 x 43.51 Shipping Weight (lbs.) 18.18 Shipping Weight (kg) 8.25 Unit Dimensions (hwd / in.) 0.000 x 0.000 x 0.000 Unit Dimensions (hwd / cm) 35.56 x 50.04 x 38.1 Unit Weight (lbs.) 11.00 Unit Weight (kg) 4.99 Weight Capacity - Stationary (kg) 16 Weight Capacity - Stationary (lbs.) 35 Number of Vertical Mounting Rails 2 Assembly Required Yes FEATURES & SPECIFICATIONS Built-in Cable Management No Extra Wide No Pre-Installed Casters No STANDARDS & COMPLIANCE Product Certifications IEC 60297-3 Product Compliance RoHS; EIA/ECA-310-E
Tripp Lite series Wall-Mount Double Shelf for IT Equipment, 20 in. Wide, Up to 250 lb. (113 kg) | Ideal alternative to a wall-mount rack enclosure Perforated shelves support maximum equipment load up to 250 lb. Keyhole mounting slots spaced 16 in. apart to match standard wall-stud placement Steel construction with smooth edges and rubber grommets for cable entry Designed for easy assembly using included hardware 5-year limited warranty. Also Available in SRWOSHELFSM
SRX12UBFFD | UPC Code 037332204073 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Small Enclosure INPUT Nominal Input Voltage(s) Supported 230V AC Nominal Input Voltage Description 230V 50/60 Hz Input Plug Type Schuko; BS1363; C14 Input Cord Length (ft.) 6 Input Cord Length (m) 1.83 PHYSICAL Color Black Rack Height 12U Rack Depth Mid Factory Preset Rack Depth (in.) 10.42 Factory Preset Rack Depth (cm) 26.5 Factory Preset Rack Depth (mm) 265 Maximum Device Depth (cm) 82.55 Maximum Device Depth (in.) 32.5 Maximum Device Depth (mm) 826 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Shipping Dimensions (hwd / in.) 30.90 x 25.00 x 39.80 Shipping Dimensions (hwd / cm) 78.49 x 63.50 x 101.09 Shipping Weight (lbs.) 136.00 Shipping Weight (kg) 61.69 Unit Dimensions (hwd / in.) 25.200 x 23.600 x 38.500 Unit Dimensions (hwd / cm) 64 x 59,95 x 97,79 Unit Weight (lbs.) 96 Unit Weight (kg) 43.54 Weight Capacity - Rolling (kg) 454 Weight Capacity - Rolling (lbs.) 1000 Weight Capacity - Stationary (kg) 454 Weight Capacity - Stationary (lbs.) 1000 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and back door frames Built-in Cable Management No Extra Wide No Locking No Pre-Installed Casters Yes Outdoor Use No STANDARDS & COMPLIANCE Protection Rating IP54 Product Compliance RoHS; EIA/ECA-310-E
SRX42UBDPWD | UPC Code 037332224361 Device Compatibility Patch Panel; Network Switch; UPS; Server Rack Type Enclosure PHYSICAL Color Black Rack Height 42U Rack Depth Deep Factory Preset Rack Depth (in.) 28.125 Factory Preset Rack Depth (cm) 71.4 Factory Preset Rack Depth (mm) 714 Maximum Device Depth (cm) 104.98 Maximum Device Depth (in.) 41.33 Maximum Device Depth (mm) 1,050 Minimum Device Depth (cm) 10.16 Minimum Device Depth (in.) 4 Minimum Device Depth (mm) 102 Shipping Dimensions (hwd / in.) 83.42 x 33.46 x 50.72 Shipping Dimensions (hwd / cm) 211.89 x 85.00 x 128.83 Shipping Weight (lbs.) 422.55 Shipping Weight (kg) 191.67 Unit Dimensions (hwd / in.) 78.500 x 31.496 x 49.060 Unit Dimensions (hwd / cm) 199,39 x 80,00 x 124,61 Unit Weight (lbs.) 374.580 Unit Weight (kg) 169.91 Weight Capacity - Rolling (kg) 1,021 Weight Capacity - Rolling (lbs.) 2250 Weight Capacity - Stationary (kg) 1,588 Weight Capacity - Stationary (lbs.) 3500 Number of Vertical Mounting Rails 4 FEATURES & SPECIFICATIONS Grounding Details Front and Back door frames Built-in Cable Management No Extra Wide Yes Pre-Installed Casters Yes STANDARDS & COMPLIANCE Product Certifications UL 60950-1 Product Compliance RoHS; CE (Europe); UKCA
47U Server Rack, Euro-Series - Expandable Cabinet, Standard Depth, Side Panels Not Included | 47U rack constructed frompowder-coated steel that stands up to tough environments Front and split rear doors locksecurely to help prevent damage, tampering or theft Ships fully assembled for quickdeployment on pre-installed casters Comes without side panels foreasy baying with multiple rack cabinets in a row Mounting rails accept standardrack equipment up to 850 mm deep. Also Available in SRX42UBEXP
SRP-R-C12 | UPC Code 037332287786 Device Compatibility PDU; Patch Panel; Server; UPS INPUT Input Connection Type 3-wire / 4-wire + Ground Voltage Compatibility (VAC) 208 Input Frequency 60 Hz COOLING Airflow 1,475 CFM Cooling Type Active Cooling Capacity (BTUs) 43686 Cooling Capacity (kW) 12.8 Refrigerant R410A Full Cooling Specifications Direct Expansion (DX) USER INTERFACE, ALERTS & CONTROLS Front Panel LCD Display 7-inch color touchscreen PHYSICAL Color Black Rack Height 44U Rack Depth Deep Maximum Device Depth (cm) 123.70 Maximum Device Depth (in.) 48.7 Maximum Device Depth (mm) 1,237 Unit Dimensions (hwd / in.) 95.070 x 40.390 x 64.880 Unit Weight (lbs.) 1407 Unit Weight (kg) 638.20 Weight Capacity - Stationary (kg) 1,361 Weight Capacity - Stationary (lbs.) 3000 Complete Configuration Dimensions (hwd / in.) 95.070 x 40.390 x 64.880 Complete Configuration Dimensions (hwd / cm) 241.48 x 102.59 x 164.80 ENVIRONMENTAL Operating Temperature Range 64° to 104°F (18° to 40°C) Storage Temperature Range -40° to 140°F (-40° to 60°C) Operating Elevation 0-13123 ft. (0-4000 m) Audible Noise < 68 DBA Operating Humidity Range 5 to 80% RH Condensate Drain Pumps (L/HR) 9 liters/hr per cooling unit Condensate Water Drains Yes FEATURES & SPECIFICATIONS Grounding Details Front and back door frames Compressor Type Rotary (Inverter Driven) Sound Level (Noise) < 68 DBA Ingress Protection (IP) Rating IP54 Built-in Cable Management Yes Extra Wide No Fans (Type/Quantity) EC 0-2000 RPM x 3 Locking Yes Pre-Installed Casters Yes Outdoor Use No STANDARDS & COMPLIANCE Product Compliance FCC Part 15 Class A (USA); RoHS
SRN3RG6U | UPC Code 037332276827 Device Compatibility Computer; DVR; Network Switch; PDU; Patch Panel; Server; UPS Rack Type Small Enclosure INPUT Nominal Input Voltage(s) Supported 120V AC Nominal Input Voltage Description 120 VAC (80VAC ~140VAC), 50Hz/60Hz Input Plug Type NEMA 5-15P Input Cord Length (ft.) 6 Input Cord Length (m) 1.83 PHYSICAL Color Gray Material of Construction Powder Coated Steel Rack Height 6U Rack Depth Mid Mounting Location Wall Factory Preset Rack Depth (in.) 20.00 Factory Preset Rack Depth (cm) 50.8 Factory Preset Rack Depth (mm) 508 Mounting Holes or Slots Yes Maximum Device Depth (cm) 45.72 Maximum Device Depth (in.) 18 Maximum Device Depth (mm) 457 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Shipping Form Factor Factory Assembled Shipping Dimensions (hwd / in.) 24.00 x 24.60 x 29.00 Shipping Dimensions (hwd / cm) 60.96 x 62.48 x 73.66 Shipping Weight (lbs.) 125.00 Shipping Weight (kg) 56.70 Unit Dimensions (hwd / in.) 17.990 x 25.170 x 20.760 Unit Dimensions (hwd / cm) 45.69 x 63.93 X 52.73 Unit Dimensions (in.) 17.990 x 25.170 x 20.760 Unit Weight (lbs.) 73.53 Unit Weight (kg) 33.35 Weight Capacity - Stationary (kg) 91 Weight Capacity - Stationary (lbs.) 200 Number of Vertical Mounting Rails 4 Mounting Details Adjustable equipment mounting rail (10-32) Cable Entry/Exit Sealed cut-out; compatible gland plates sold separately. FEATURES & SPECIFICATIONS Grounding Details Cabinet Body Tools Necessary Yes Built-in Cable Management Yes Extra Wide No Fans (Type/Quantity) 7 x 5.9-in/150 mm fan; PBT blades; Aluminum frame; 190/210 CFM Fan Details NOTE: Fans only activate when the ambient temperature inside the enclosure exceeds 86°F (30°C) Locking Yes Lock Type Key Pre-Installed Casters No Outdoor Use Yes Gasketed Door Yes STANDARDS & COMPLIANCE Protection Rating NEMA 3R Product Certifications CAN/CSA-C22.2 No. 286 (Canada); UL 508A Product Compliance RoHS; REACH; EIA/ECA-310-E; NEMA 3R
SRN3RR6U | UPC Code 037332278050 Device Compatibility Computer; DVR; Network Switch; PDU; Patch Panel; Server; UPS Rack Type Small Enclosure INPUT Nominal Input Voltage(s) Supported 120V AC Nominal Input Voltage Description 120 VAC (80VAC ~140VAC), 50Hz/60Hz Input Plug Type NEMA 5-15P Input Cord Length (ft.) 6 Input Cord Length (m) 1.83 PHYSICAL Color Red Material of Construction Powder Coated Steel Rack Height 6U Rack Depth Mid Mounting Location Wall Factory Preset Rack Depth (in.) 20.00 Factory Preset Rack Depth (cm) 50.8 Factory Preset Rack Depth (mm) 508 Mounting Holes or Slots Yes Maximum Device Depth (cm) 45.72 Maximum Device Depth (in.) 18 Maximum Device Depth (mm) 457 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Shipping Form Factor Factory Assembled Shipping Dimensions (hwd / in.) 24.00 x 24.60 x 29.00 Shipping Dimensions (hwd / cm) 60.96 x 62.48 x 73.66 Shipping Weight (lbs.) 125.00 Shipping Weight (kg) 56.70 Unit Dimensions (hwd / in.) 17.990 x 25.170 x 20.760 Unit Dimensions (hwd / cm) 45.69 x 63.93 X 52.73 Unit Dimensions (in.) 17.990 x 25.170 x 20.760 Unit Weight (lbs.) 73.53 Unit Weight (kg) 33.35 Weight Capacity - Stationary (kg) 91 Weight Capacity - Stationary (lbs.) 200 Number of Vertical Mounting Rails 4 Mounting Details Adjustable equipment mounting rail (10-32) Cable Entry/Exit Sealed cut-out; compatible gland plates sold separately. FEATURES & SPECIFICATIONS Grounding Details Cabinet Body Tools Necessary Yes Built-in Cable Management Yes Extra Wide No Fans (Type/Quantity) 14 x 5.9-in/150 mm fan; PBT blades; Aluminum frame; 190/210 CFM Fan Details NOTE: Fans only activate when the ambient temperature inside the enclosure exceeds 86°F (30°C) Locking Yes Lock Type Key Pre-Installed Casters No Outdoor Use Yes Gasketed Door Yes STANDARDS & COMPLIANCE Protection Rating NEMA 3R Product Certifications CAN/CSA-C22.2 No. 286 (Canada); UL 508A Product Compliance RoHS; REACH; EIA/ECA-310-E; NEMA 3R
SRN3RG12U | UPC Code 037332276841 Device Compatibility Computer; DVR; Network Switch; PDU; Patch Panel; Server; UPS Rack Type Enclosure INPUT Nominal Input Voltage(s) Supported 120V AC Nominal Input Voltage Description 120 VAC (80VAC ~140VAC), 50Hz/60Hz Input Plug Type NEMA 5-15P Input Cord Length (ft.) 6 Input Cord Length (m) 1.83 PHYSICAL Color Gray Material of Construction Powder Coated Steel Rack Height 12U Rack Depth Mid Mounting Location Wall Factory Preset Rack Depth (in.) 20.00 Factory Preset Rack Depth (cm) 50.8 Factory Preset Rack Depth (mm) 508 Mounting Holes or Slots Yes Maximum Device Depth (cm) 59.69 Maximum Device Depth (in.) 23.5 Maximum Device Depth (mm) 597 Minimum Device Depth (cm) 7.62 Minimum Device Depth (in.) 3 Minimum Device Depth (mm) 76 Shipping Form Factor Factory Assembled Shipping Dimensions (hwd / in.) 34.53 x 28.00 x 31.00 Shipping Dimensions (hwd / cm) 87.71 x 71.12 x 78.74 Shipping Weight (lbs.) 175.00 Shipping Weight (kg) 79.38 Unit Dimensions (hwd / in.) 28.070 x 24.000 x 27.190 Unit Dimensions (hwd / cm) 72.360 x 63.930 X 70.430 Unit Dimensions (in.) 28.490 x 25.170 x 27.730 Unit Weight (lbs.) 96.280 Unit Weight (kg) 43.67 Weight Capacity - Stationary (kg) 91 Weight Capacity - Stationary (lbs.) 200 Number of Vertical Mounting Rails 4 Mounting Details Adjustable equipment mounting rail (10-32) Cable Entry/Exit Sealed cut-out; compatible gland plates sold separately. FEATURES & SPECIFICATIONS Grounding Details Cabinet Body Tools Necessary Yes Built-in Cable Management Yes Extra Wide No Fans (Type/Quantity) 2 x 5.9-in/150 mm fan; PBT blades; Aluminum frame; 190/210 CFM Fan Details NOTE: Fans only activate when the ambient temperature inside the enclosure exceeds 86°F (30°C) Locking Yes Lock Type Key Pre-Installed Casters No Outdoor Use Yes Gasketed Door Yes STANDARDS & COMPLIANCE Protection Rating NEMA 3R Product Certifications CAN/CSA-C22.2 No. 286 (Canada); UL 508A Product Compliance RoHS; REACH; EIA/ECA-310-E; NEMA 3R